## 1s Summary of Results
| Building Area (ft2): | 211975
1A - Miami | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 4862049 | 3668625 | 2993656 | 175825 | 2023218 | 5658694 | 0 | 234168 | 345722 | 34299 | 1228691 | 19996256 | 94.3331 | max EUI | max EUI
| TMY3 DOE | 4890539 | 3827404 | 2993656 | 178641 | 2023218 | 5663907 | 0 | 244302 | 345722 | 34299 | 1228691 | 20201688 | 95.3022 | 98.742 | 95.5797
| TMY3 WA | 4057460 | 4576784 | 2993656 | 180906 | 2023218 | 5756333 | 0 | 292135 | 345722 | 34299 | 1228691 | 20260513 | 95.5797 | min EUI | min EUI
| TMY7 WA | 4376045 | 4080966 | 2993656 | 182207 | 2023218 | 5694057 | 0 | 260487 | 345722 | 34299 | 1228691 | 19990657 | 94.3067 | 93.0186 | 93.0186
| TMY15 WA | 3945697 | 4202866 | 2993656 | 181525 | 2023218 | 5722377 | 0 | 268268 | 345722 | 34299 | 1228691 | 19717628 | 93.0186 | variance | variance
| XMY Min WA | 7146193 | 2714972 | 2993656 | 183602 | 2023218 | 5315876 | 0 | 173296 | 345722 | 34299 | 1228691 | 20930834 | 98.742 | 6.005% | 2.687%
| XMY Max WA | 3636530 | 4976122 | 2993656 | 178359 | 2023218 | 5797453 | 0 | 317625 | 345722 | 34299 | 1228691 | 20302984 | 95.7801
2A - Houston | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5429043 | 2928596 | 2993656 | 177640 | 2023218 | 5204701 | 0 | 186932 | 345722 | 34299 | 1228691 | 19323807 | 91.1608 | max EUI | max EUI
| TMY3 DOE | 5292256 | 2970949 | 2993656 | 179554 | 2023218 | 5243975 | 0 | 189635 | 345722 | 34299 | 1228691 | 19273264 | 90.9223 | 99.3676 | 91.1608
| TMY3 WA | 3551780 | 3535158 | 2993656 | 186049 | 2023218 | 5344202 | 0 | 225648 | 345722 | 34299 | 1228691 | 18239732 | 86.0466 | min EUI | min EUI
| TMY7 WA | 4210714 | 3258072 | 2993656 | 186368 | 2023218 | 5300963 | 0 | 207962 | 345722 | 34299 | 1228691 | 18560974 | 87.5621 | 84.3488 | 86.0466
| TMY15 WA | 4199053 | 3401048 | 2993656 | 185961 | 2023218 | 5337760 | 0 | 217088 | 345722 | 34299 | 1228691 | 18737805 | 88.3963 | variance | variance
| XMY Min WA | 8665233 | 1973829 | 2993656 | 195846 | 2023218 | 4705648 | 0 | 125989 | 345722 | 34299 | 1228691 | 21063440 | 99.3676 | 16.52% | 5.625%
| XMY Max WA | 2342041 | 4239085 | 2993656 | 183590 | 2023218 | 5447643 | 0 | 270580 | 345722 | 34299 | 1228691 | 17879834 | 84.3488
2B - Phoenix | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1328146 | 3982335 | 2993656 | 175394 | 2023218 | 2331255 | 0 | 254192 | 345722 | 34299 | 1228691 | 13468217 | 63.5368 | max EUI | max EUI
| TMY3 DOE | 1074920 | 4305481 | 2993656 | 177114 | 2023218 | 2393019 | 0 | 274818 | 345722 | 34299 | 1228691 | 13622247 | 64.2635 | 66.6416 | 64.2635
| TMY3 WA | 1012089 | 4356505 | 2993656 | 181625 | 2023218 | 2369011 | 0 | 278075 | 345722 | 34299 | 1228691 | 13594200 | 64.1311 | min EUI | min EUI
| TMY7 WA | 1091363 | 3962409 | 2993656 | 180843 | 2023218 | 2324363 | 0 | 252920 | 345722 | 34299 | 1228691 | 13208793 | 62.313 | 62.313 | 62.313
| TMY15 WA | 1096484 | 4162570 | 2993656 | 181125 | 2023218 | 2362345 | 0 | 265696 | 345722 | 34299 | 1228691 | 13465115 | 63.5222 | variance | variance
| XMY Min WA | 2822401 | 2481233 | 2993656 | 181419 | 2023218 | 2250048 | 0 | 158377 | 345722 | 34299 | 1228691 | 13290373 | 62.6978 | 6.736% | 3.035%
| XMY Max WA | 597239 | 5139998 | 2993656 | 179385 | 2023218 | 2484750 | 0 | 328085 | 345722 | 34299 | 1228691 | 14126352 | 66.6416
3A - Atlanta | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 7226117 | 1788091 | 2993656 | 177771 | 2023218 | 4797125 | 0 | 114133 | 345722 | 34299 | 1228691 | 19500132 | 91.9926 | max EUI | max EUI
| TMY3 DOE | 6824521 | 1922641 | 2993656 | 180756 | 2023218 | 4820655 | 0 | 122722 | 345722 | 34299 | 1228691 | 19268190 | 90.8984 | 102.4337 | 91.9926
| TMY3 WA | 5467427 | 2329494 | 2993656 | 188858 | 2023218 | 4917061 | 0 | 148691 | 345722 | 34299 | 1228691 | 18448426 | 87.0311 | min EUI | min EUI
| TMY7 WA | 6140254 | 2107148 | 2993656 | 189208 | 2023218 | 4856254 | 0 | 134499 | 345722 | 34299 | 1228691 | 18824258 | 88.8041 | 81.8896 | 86.794
| TMY15 WA | 5592900 | 2182318 | 2993656 | 188094 | 2023218 | 4898663 | 0 | 139297 | 345722 | 34299 | 1228691 | 18398167 | 86.794 | variance | variance
| XMY Min WA | 10712142 | 1038231 | 2993656 | 187506 | 2023218 | 4312350 | 0 | 66270 | 345722 | 34299 | 1228691 | 21713394 | 102.4337 | 22.6% | 5.719%
| XMY Max WA | 3587389 | 2923218 | 2993656 | 189433 | 2023218 | 5075033 | 0 | 186588 | 345722 | 34299 | 1228691 | 17358556 | 81.8896
3B - Las Vegas | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1623262 | 2815662 | 2993656 | 174724 | 2023218 | 1948237 | 0 | 179723 | 345722 | 34299 | 1228691 | 12138503 | 57.2638 | max EUI | max EUI
| TMY3 DOE | 1652101 | 2928436 | 2993656 | 177559 | 2023218 | 1965897 | 0 | 186921 | 345722 | 34299 | 1228691 | 12307809 | 58.0625 | 60.9452 | 58.7084
| TMY3 WA | 1538715 | 3136709 | 2993656 | 180956 | 2023218 | 1991231 | 0 | 200215 | 345722 | 34299 | 1228691 | 12444721 | 58.7084 | min EUI | min EUI
| TMY7 WA | 1587665 | 2906382 | 2993656 | 180831 | 2023218 | 1957427 | 0 | 185514 | 345722 | 34299 | 1228691 | 12214714 | 57.6234 | 57.2638 | 57.2638
| TMY15 WA | 1621863 | 2942031 | 2993656 | 180906 | 2023218 | 1968296 | 0 | 187789 | 345722 | 34299 | 1228691 | 12297780 | 58.0152 | variance | variance
| XMY Min WA | 3958427 | 1477173 | 2993656 | 180599 | 2023218 | 1811468 | 0 | 94288 | 345722 | 34299 | 1228691 | 12918850 | 60.9452 | 6.34% | 2.488%
| XMY Max WA | 935659 | 4027663 | 2993656 | 179980 | 2023218 | 2119024 | 0 | 257085 | 345722 | 34299 | 1228691 | 12916306 | 60.9332
3C - San Francisco | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 9047887 | 672296 | 1892969 | 179911 | 1213937 | 3940403 | 0 | 42912 | 345722 | 34299 | 1228691 | 17370336 | 81.9452 | max EUI | max EUI
| TMY3 DOE | 8637653 | 749649 | 1892969 | 181650 | 1213937 | 4009935 | 0 | 47850 | 345722 | 34299 | 1228691 | 17113664 | 80.7344 | 88.7546 | 82.6112
| TMY3 WA | 7508169 | 825020 | 1892969 | 185980 | 1213937 | 4110782 | 0 | 52661 | 345722 | 34299 | 1228691 | 16169539 | 76.2804 | min EUI | min EUI
| TMY7 WA | 9087022 | 730573 | 1892969 | 188245 | 1213937 | 3972109 | 0 | 46632 | 345722 | 34299 | 1228691 | 17511508 | 82.6112 | 71.1651 | 76.2804
| TMY15 WA | 8308162 | 692782 | 1892969 | 187331 | 1213937 | 4011100 | 0 | 44220 | 345722 | 34299 | 1228691 | 16730522 | 78.9269 | variance | variance
| XMY Min WA | 10880684 | 461897 | 1892969 | 183577 | 1213937 | 3771193 | 0 | 29483 | 345722 | 34299 | 1228691 | 18813761 | 88.7546 | 21.79% | 7.842%
| XMY Max WA | 6172578 | 926792 | 1892969 | 183202 | 1213937 | 4256559 | 0 | 59157 | 345722 | 34299 | 1228691 | 15085215 | 71.1651
4A - Baltimore | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 7405175 | 2266817 | 2993656 | 182245 | 2023218 | 2092020 | 21723 | 144690 | 345722 | 34299 | 1228691 | 17509565 | 82.602 | max EUI | max EUI
| TMY3 DOE | 6807065 | 2309071 | 2993656 | 182689 | 2023218 | 2059238 | 20115 | 147388 | 345722 | 34299 | 1228691 | 16922461 | 79.8323 | 106.3569 | 82.602
| TMY3 WA | 4793612 | 2757150 | 2993656 | 190372 | 2023218 | 1999415 | 14744 | 175988 | 345722 | 34299 | 1228691 | 15328176 | 72.3112 | min EUI | min EUI
| TMY7 WA | 5671809 | 2563716 | 2993656 | 191116 | 2023218 | 2028074 | 17076 | 163641 | 345722 | 34299 | 1228691 | 16032327 | 75.6331 | 65.4867 | 72.3112
| TMY15 WA | 5075102 | 2719630 | 2993656 | 189302 | 2023218 | 2024349 | 15466 | 173593 | 345722 | 34299 | 1228691 | 15594337 | 73.5669 | variance | variance
| XMY Min WA | 12907744 | 1583149 | 2993656 | 193519 | 2023218 | 2327150 | 35501 | 101052 | 345722 | 34299 | 1228691 | 22545010 | 106.3569 | 51.2% | 12.89%
| XMY Max WA | 2545605 | 3628514 | 2993656 | 191273 | 2023218 | 1879698 | 7942 | 231607 | 345722 | 34299 | 1228691 | 13881534 | 65.4867
4B - Albuquerque | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5885364 | 1739300 | 2993656 | 176995 | 2023218 | 2118472 | 18425 | 111019 | 345722 | 34299 | 1228691 | 15446470 | 72.8693 | max EUI | max EUI
| TMY3 DOE | 5481108 | 1722146 | 2993656 | 178747 | 2023218 | 2088236 | 17380 | 109924 | 345722 | 34299 | 1228691 | 14994436 | 70.7368 | 101.1248 | 73.926
| TMY3 WA | 4747018 | 2018635 | 2993656 | 180756 | 2023218 | 2122588 | 15712 | 128849 | 345722 | 34299 | 1228691 | 14610453 | 68.9254 | min EUI | min EUI
| TMY7 WA | 5802091 | 1962124 | 2993656 | 181037 | 2023218 | 2184600 | 18484 | 125242 | 345722 | 34299 | 1228691 | 15670473 | 73.926 | 63.8269 | 68.9254
| TMY15 WA | 5601173 | 2000099 | 2993656 | 181043 | 2023218 | 2164815 | 17985 | 127666 | 345722 | 34299 | 1228691 | 15489676 | 73.0731 | variance | variance
| XMY Min WA | 11904299 | 1416223 | 2993656 | 181150 | 2023218 | 2413305 | 33650 | 90397 | 345722 | 34299 | 1228691 | 21435919 | 101.1248 | 52.73% | 7.069%
| XMY Max WA | 3352817 | 2393839 | 2993656 | 179748 | 2023218 | 2041908 | 11711 | 152798 | 345722 | 34299 | 1228691 | 13529716 | 63.8269
4C - Portland | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 6566517 | 1376326 | 2993656 | 184760 | 2023218 | 1969990 | 19419 | 87851 | 345722 | 34299 | 1228691 | 15601758 | 73.6019 | max EUI | max EUI
| TMY3 DOE | 6227265 | 1424370 | 2993656 | 186856 | 2023218 | 1952813 | 18475 | 90917 | 345722 | 34299 | 1228691 | 15297591 | 72.167 | 106.552 | 76.4833
| TMY3 WA | 5721720 | 1589342 | 2993656 | 199050 | 2023218 | 1960342 | 17452 | 101447 | 345722 | 34299 | 1228691 | 14986248 | 70.6982 | min EUI | min EUI
| TMY7 WA | 6778694 | 1639621 | 2993656 | 195840 | 2023218 | 2076733 | 20101 | 104657 | 345722 | 34299 | 1228691 | 16212541 | 76.4833 | 63.0733 | 70.6982
| TMY15 WA | 6204227 | 1628971 | 2993656 | 196879 | 2023218 | 2014925 | 18794 | 103977 | 345722 | 34299 | 1228691 | 15564668 | 73.4269 | variance | variance
| XMY Min WA | 13159285 | 1249358 | 2993656 | 194088 | 2023218 | 2471222 | 35771 | 79746 | 345722 | 34299 | 1228691 | 22586365 | 106.552 | 60.25% | 8.016%
| XMY Max WA | 3672792 | 2096573 | 2993656 | 199563 | 2023218 | 1858253 | 12061 | 133824 | 345722 | 34299 | 1228691 | 13369961 | 63.0733
5A - Chicago | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 10392723 | 1969700 | 2993656 | 181694 | 2023218 | 2237437 | 30940 | 125726 | 345722 | 34299 | 1228691 | 20335115 | 95.9317 | max EUI | max EUI
| TMY3 DOE | 10175805 | 2038311 | 2993656 | 183540 | 2023218 | 2224411 | 30350 | 130105 | 345722 | 34299 | 1228691 | 20179417 | 95.1972 | 130.434 | 95.9317
| TMY3 WA | 6984728 | 2212010 | 2993656 | 191961 | 2023218 | 2066133 | 22085 | 141192 | 345722 | 34299 | 1228691 | 17015004 | 80.2689 | min EUI | min EUI
| TMY7 WA | 8728451 | 2102736 | 2993656 | 190991 | 2023218 | 2173343 | 26846 | 134217 | 345722 | 34299 | 1228691 | 18753479 | 88.4702 | 69.8844 | 80.2689
| TMY15 WA | 8037504 | 2188747 | 2993656 | 190691 | 2023218 | 2139592 | 24665 | 139707 | 345722 | 34299 | 1228691 | 18117801 | 85.4714 | variance | variance
| XMY Min WA | 17980871 | 1428928 | 2993656 | 188582 | 2023218 | 2512434 | 49827 | 91208 | 345722 | 34299 | 1228691 | 27648745 | 130.434 | 63.6% | 16.45%
| XMY Max WA | 4419184 | 2665133 | 2993656 | 193406 | 2023218 | 1954610 | 14406 | 170115 | 345722 | 34299 | 1228691 | 14813749 | 69.8844
5B - Boulder | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 7573243 | 1243956 | 2993656 | 179448 | 2023218 | 1935588 | 23685 | 79401 | 345722 | 34299 | 1228691 | 16432216 | 77.5196 | max EUI | max EUI
| TMY3 DOE | 7123126 | 1236388 | 2993656 | 181775 | 2023218 | 1923058 | 22564 | 78918 | 345722 | 34299 | 1228691 | 15962724 | 75.3047 | 134.7605 | 82.647
| TMY3 WA | 8518525 | 1153717 | 2993656 | 182708 | 2023218 | 2027887 | 26816 | 73642 | 345722 | 34299 | 1228691 | 17380190 | 81.9917 | min EUI | min EUI
| TMY7 WA | 8640026 | 1167864 | 2993656 | 182795 | 2023218 | 2030259 | 26723 | 74545 | 345722 | 34299 | 1228691 | 17519107 | 82.647 | 65.8285 | 75.3047
| TMY15 WA | 8267657 | 1188333 | 2993656 | 182320 | 2023218 | 2019943 | 26087 | 75851 | 345722 | 34299 | 1228691 | 17157086 | 80.9392 | variance | variance
| XMY Min WA | 19730340 | 813095 | 2993656 | 185905 | 2023218 | 2334204 | 53524 | 51900 | 345722 | 34299 | 1228691 | 28565863 | 134.7605 | 91.54% | 9.75%
| XMY Max WA | 4805008 | 1556965 | 2993656 | 180405 | 2023218 | 1898846 | 16492 | 99381 | 345722 | 34299 | 1228691 | 13953992 | 65.8285
5C - Vancouver | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
[15 empty] | max EUI | max EUI
| CWEC | 8106779 | 1023072 | 2993656 | 197873 | 2023218 | 2073468 | 24280 | 65302 | 345722 | 34299 | 1228691 | 16887669 | 79.6682 | 108.1694 | 81.055
| TMY3 WA | 6477182 | 1100452 | 2993656 | 198124 | 2023218 | 1954191 | 19983 | 70242 | 345722 | 34299 | 1228691 | 15217069 | 71.7871 | min EUI | min EUI
| TMY7 WA | 8387376 | 1001117 | 2993656 | 200013 | 2023218 | 2107256 | 25086 | 63901 | 345722 | 34299 | 1228691 | 17181644 | 81.055 | 65.2908 | 71.7871
| TMY15 WA | 7486063 | 1026995 | 2993656 | 199782 | 2023218 | 2035425 | 22922 | 65553 | 345722 | 34299 | 1228691 | 16233635 | 76.5828 | variance | variance
| XMY Min WA | 13956088 | 875058 | 2993656 | 194764 | 2023218 | 2412715 | 37840 | 55855 | 345722 | 34299 | 1228691 | 22929215 | 108.1694 | 53.82% | 11.63%
| XMY Max WA | 5112883 | 1185185 | 2993656 | 201408 | 2023218 | 1851334 | 16670 | 75650 | 345722 | 34299 | 1228691 | 13840025 | 65.2908
6A - Minneapolis | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 13132793 | 1887247 | 2993656 | 182007 | 2023218 | 2327139 | 37966 | 120463 | 345722 | 34299 | 1228691 | 23084510 | 108.902 | max EUI | max EUI
| TMY3 DOE | 12663344 | 1843152 | 2993656 | 184378 | 2023218 | 2318081 | 37733 | 117648 | 345722 | 34299 | 1228691 | 22561231 | 106.4335 | 151.6482 | 108.902
| TMY3 WA | 8623816 | 2178361 | 2993656 | 192587 | 2023218 | 2172141 | 27229 | 139044 | 345722 | 34299 | 1228691 | 18730073 | 88.3598 | min EUI | min EUI
| TMY7 WA | 11768435 | 2002474 | 2993656 | 192030 | 2023218 | 2318071 | 35454 | 127817 | 345722 | 34299 | 1228691 | 21841176 | 103.0366 | 78.4696 | 88.3598
| TMY15 WA | 10039641 | 2091294 | 2993656 | 192430 | 2023218 | 2239986 | 30667 | 133487 | 345722 | 34299 | 1228691 | 20124400 | 94.9376 | variance | variance
| XMY Min WA | 22366805 | 1402141 | 2993656 | 191010 | 2023218 | 2638376 | 60910 | 89498 | 345722 | 34299 | 1228691 | 32145635 | 151.6482 | 68.76% | 19.3%
| XMY Max WA | 5898596 | 2827004 | 2993656 | 193137 | 2023218 | 2118047 | 19469 | 180447 | 345722 | 34299 | 1228691 | 16633595 | 78.4696
6B - Helena | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 11873111 | 1219094 | 2993656 | 181619 | 2023218 | 2218508 | 37646 | 77815 | 345722 | 34299 | 1228691 | 21004688 | 99.0904 | max EUI | max EUI
| TMY3 DOE | 11370295 | 1221561 | 2993656 | 183183 | 2023218 | 2219284 | 36688 | 77972 | 345722 | 34299 | 1228691 | 20505878 | 96.7372 | 160.9982 | 99.0904
| TMY3 WA | 10307316 | 1535844 | 2993656 | 187769 | 2023218 | 2289522 | 34591 | 98033 | 345722 | 34299 | 1228691 | 19849970 | 93.643 | min EUI | min EUI
| TMY7 WA | 892340 | 6452874 | 2993656 | 184134 | 2023218 | 1971649 | 2292 | 411886 | 345722 | 34299 | 1228691 | 15312070 | 72.2353 | 72.2353 | 72.2353
| TMY15 WA | 11060089 | 1431051 | 2993656 | 187976 | 2023218 | 2300545 | 36563 | 91344 | 345722 | 34299 | 1228691 | 20504463 | 96.7306 | variance | variance
| XMY Min WA | 24530611 | 1138746 | 2993656 | 188683 | 2023218 | 2731021 | 68944 | 72686 | 345722 | 34299 | 1228691 | 34127586 | 160.9982 | 91.76% | 27.76%
| XMY Max WA | 7454752 | 1767848 | 2993656 | 185698 | 2023218 | 2132137 | 26179 | 112841 | 345722 | 34299 | 1228691 | 17076350 | 80.5583
7 - Duluth | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 16025875 | 1371173 | 2993656 | 181744 | 2023218 | 2422833 | 46377 | 87522 | 345722 | 34299 | 1228691 | 25532419 | 120.4501 | max EUI | max EUI
| TMY3 DOE | 15234728 | 1386455 | 2993656 | 184084 | 2023218 | 2390799 | 44732 | 88497 | 345722 | 34299 | 1228691 | 24726190 | 116.6467 | 158.2431 | 120.4501
| TMY3 WA | 9898351 | 1755331 | 2993656 | 195014 | 2023218 | 2216962 | 31390 | 112042 | 345722 | 34299 | 1228691 | 19605985 | 92.492 | min EUI | min EUI
| TMY7 WA | 12775703 | 1639300 | 2993656 | 194789 | 2023218 | 2355014 | 38742 | 104636 | 345722 | 34299 | 1228691 | 22505079 | 106.1686 | 81.2501 | 92.492
| TMY15 WA | 10954791 | 1665269 | 2993656 | 193819 | 2023218 | 2257239 | 33995 | 106294 | 345722 | 34299 | 1228691 | 20608302 | 97.2204 | variance | variance
| XMY Min WA | 23930275 | 1207061 | 2993656 | 192124 | 2023218 | 2675120 | 65054 | 77046 | 345722 | 34299 | 1228691 | 33543575 | 158.2431 | 66.01% | 23.97%
| XMY Max WA | 7132856 | 2220993 | 2993656 | 197235 | 2023218 | 2109643 | 23597 | 141766 | 345722 | 34299 | 1228691 | 17222985 | 81.2501
8 - Fairbanks | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 24487705 | 936473 | 2993656 | 202309 | 2023218 | 2563879 | 68765 | 59775 | 345722 | 34299 | 1228691 | 33715801 | 159.0556 | max EUI | max EUI
| TMY3 DOE | 22148273 | 962314 | 2993656 | 203529 | 2023218 | 2524813 | 64067 | 61424 | 345722 | 34299 | 1228691 | 31361315 | 147.9482 | 211.018 | 159.0556
| TMY3 WA | 16294643 | 1162983 | 2993656 | 205713 | 2023218 | 2428612 | 51368 | 74233 | 345722 | 34299 | 1228691 | 25614447 | 120.8371 | min EUI | min EUI
| TMY7 WA | 20131898 | 1050604 | 2993656 | 205813 | 2023218 | 2533506 | 61011 | 67060 | 345722 | 34299 | 1228691 | 29446787 | 138.9163 | 101.8722 | 120.8371
| TMY15 WA | 18520238 | 1106580 | 2993656 | 206163 | 2023218 | 2480061 | 56547 | 70633 | 345722 | 34299 | 1228691 | 27837117 | 131.3226 | variance | variance
| XMY Min WA | 35180957 | 906439 | 2993656 | 208685 | 2023218 | 2886191 | 93518 | 57858 | 345722 | 34299 | 1228691 | 44730543 | 211.018 | 73.77% | 25.83%
| XMY Max WA | 12199936 | 1351740 | 2993656 | 205175 | 2023218 | 2312476 | 41848 | 86281 | 345722 | 34299 | 1228691 | 21594351 | 101.8722
1A - Miami
2A - Houston
2B - Phoenix
3A - Atlanta
3B - Las Vegas
3C - San Francisco
4A - Baltimore
4B - Albuquerque
4C - Portland
5A - Chicago
5B - Boulder
5C - Vancouver
6A - Minneapolis
6B - Helena
7 - Duluth
8 - Fairbanks

## 1s Additional Indicators
|  | PPD | [13 empty] | Predicted Percentage Dissatisfied | [9 empty] | Peak Heating Load | [9 empty] | Peak Cooling Load
Climate Zone | Climate File | FLOOR 1 | Mech | FLOOR 2 | AUDITORIUM | GYM | KITCHEN CAFETERIA | Unmet Hours (Heating) | Unmet Hours (Cooling) | UH Compliance | Peak Heating Load | Peak Cooling Load | Overheating Risk | EUI |  | Climate | [9 empty] | Climate | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | Climate | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY3WA | 91 | 35 | 95 | 30 | 22 | 28 | 0 | 1 | 1 | 1347474 | 836799 |  |  |  | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 1A | Heating plant sensible load | ASHRAE ZONING - FLOOR 1 | RL.htg | Load (Btu/h) | 1347474 | 12:00, January | 1347474 | 12:00, January | 1347474 | 1A | Cooling plant sensible load | ASHRAE ZONING - FLOOR 1 | RL.clg | Load (Btu/h) | 0 | 00:30, May | 836799 | 06:30, July | 242226
1A | TMY7WA | 86 | 32 | 93 | 26 | 19 | 25 | 2 | 1 | 3 |  |  |  |  | 1AFLOOR 1TMY3WA | 1A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 34 | 07:30,23/Jan | 99 | 16:30,10/Sep | 91 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY3 | 83 | 30 | 91 | 24 | 18 | 24 | 0 | 0 | 0 |  |  |  |  | 1AMECHTMY3WA | 1A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 07:30,23/Jan | 60 | 14:30,10/Sep | 35 | 2A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3817965 | 12:00, January | 3817965 | 12:00, January | 3817965 | 2A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 2088790 | 14:30, September | 706081
1A | TMY2 | 83 | 30 | 91 | 24 | 18 | 24 | 0 | 1 | 1 |  |  |  |  | 1AFLOOR 2TMY3WA | 1A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 60 | 00:30,01/Apr | 100 | 14:30,22/Mar | 95 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY15WA | 88 | 33 | 94 | 28 | 20 | 27 | 0 | 2 | 2 |  |  |  |  | 1AAUDITORIUMTMY3WA | 1A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 07:30,31/Mar | 67 | 15:30,22/Aug | 30 | 2B | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3335691 | 12:00, January | 3335691 | 12:00, January | 3335691 | 2B | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 33472 | 04:30, May | 2663299 | 13:30, September | 1158642
1A | MIN | 66 | 23 | 81 | 19 | 14 | 18 | 0 | 0 | 0 |  |  |  |  | 1AGYMTMY3WA | 1A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 08:30,14/Jan | 59 | 07:30,05/Sep | 22 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | MAX | 93 | 38 | 96 | 33 | 24 | 30 | 20 | 2 | 22 |  |  |  |  | 1AKITCHEN CAFETERIATMY3WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 6 | 14:30,23/Jan | 62 | 03:30,17/Aug | 28 | 3A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4088501 | 12:00, January | 4088501 | 12:00, January | 4088501 | 3A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1750283 | 14:30, September | 596672
2A | TMY7WA | 85 | 27 | 87 | 21 | 15 | 22 | 6 | 2 | 8 | 3817965 | 2088790 |  |  | 1AFLOOR 1TMY7WA | 1A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 6 | 05:30,04/Jan | 99 | 16:30,10/Sep | 86 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY3WA | 88 | 29 | 90 | 23 | 16 | 24 | 1 | 2 | 3 |  |  |  |  | 1AMECHTMY7WA | 1A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 06:30,29/Dec | 60 | 14:30,10/Sep | 32 | 3B | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3619627 | 12:00, January | 3619627 | 12:00, January | 3619627 | 3B | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 7055 | 04:30, May | 2283118 | 06:30, July | 948956
2A | TMY3 | 82 | 25 | 85 | 20 | 14 | 21 | 1 | 8 | 9 |  |  |  |  | 1AFLOOR 2TMY7WA | 1A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 18 | 07:30,03/Jan | 100 | 15:30,02/Apr | 93 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY2 | 81 | 25 | 84 | 20 | 13 | 21 | 0 | 2 | 2 |  |  |  |  | 1AAUDITORIUMTMY7WA | 1A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 02:30,29/Jan | 67 | 17:30,17/Jul | 26 | 3C | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3224919 | 12:00, January | 3224919 | 12:00, January | 3224919 | 3C | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1134247 | 16:30, September | 233197
2A | TMY15WA | 86 | 27 | 88 | 21 | 15 | 23 | 0 | 3 | 3 |  |  |  |  | 1AGYMTMY7WA | 1A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 08:30,12/Mar | 59 | 07:30,05/Sep | 19 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | MIN | 63 | 21 | 69 | 18 | 12 | 16 | 0 | 14 | 14 |  |  |  |  | 1AKITCHEN CAFETERIATMY7WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 13:30,02/Jan | 64 | 06:30,03/Jul | 25 | 4A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4186155 | 12:00, January | 4186155 | 12:00, January | 4186155 | 4A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1834987 | 14:30, September | 609641
2A | MAX | 94 | 35 | 95 | 28 | 19 | 27 | 23 | 2 | 25 |  |  |  |  | 1AFLOOR 1TMY3 | 1A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 6 | 05:30,04/Feb | 99 | 16:30,22/Sep | 83 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY7WA | 17 | 21 | 19 | 17 | 14 | 16 | 4 | 10 | 14 | 3335691 | 2663299 |  |  | 1AMECHTMY3 | 1A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 02:30,15/Dec | 56 | 14:30,09/Sep | 30 | 4B | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 3979020 | 12:00, January | 3979020 | 12:00, January | 3979020 | 4B | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1620069 | 14:30, September | 492266
2B | TMY3WA | 19 | 23 | 20 | 19 | 15 | 18 | 0 | 19 | 19 |  |  |  |  | 1AFLOOR 2TMY3 | 1A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 31 | 05:30,04/Feb | 100 | 16:30,17/May | 91 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY3 | 20 | 23 | 22 | 20 | 16 | 18 | 0 | 22 | 22 |  |  |  |  | 1AAUDITORIUMTMY3 | 1A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 01:30,20/Mar | 66 | 12:30,02/Oct | 24 | 4C | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3717431 | 12:00, January | 3717431 | 12:00, January | 3717431 | 4C | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1703772 | 14:30, September | 545748
2B | TMY2 | 19 | 22 | 21 | 19 | 15 | 17 | 0 | 17 | 17 |  |  |  |  | 1AGYMTMY3 | 1A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,14/Dec | 60 | 03:30,11/Sep | 18 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY15WA | 18 | 22 | 20 | 18 | 15 | 17 | 2 | 13 | 15 |  |  |  |  | 1AKITCHEN CAFETERIATMY3 | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 20:30,20/Dec | 63 | 01:30,30/Oct | 24 | 5A | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 4783322 | 12:00, January | 4783322 | 12:00, January | 4783322 | 5A | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1715606 | 14:30, September | 547479+BF403
2B | MIN | 16 | 18 | 17 | 15 | 12 | 13 | 0 | 25 | 25 |  |  |  |  | 1AFLOOR 1TMY2 | 1A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 6 | 01:30,13/Jan | 99 | 16:30,01/Sep | 83 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | MAX | 20 | 25 | 21 | 20 | 17 | 19 | 55 | 3 | 58 |  |  |  |  | 1AMECHTMY2 | 1A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 04:30,31/Jan | 52 | 16:30,09/Sep | 30 | 5B | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4593129 | 12:00, January | 4593129 | 12:00, January | 4593129 | 5B | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1623303 | 14:30, September | 435957
3A | TMY7WA | 74 | 22 | 78 | 17 | 12 | 17 | 47 | 5 | 52 | 4088501 | 1750283 |  |  | 1AFLOOR 2TMY2 | 1A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 15 | 04:30,04/Jan | 100 | 15:30,19/May | 91 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY3WA | 78 | 23 | 82 | 17 | 12 | 18 | 29 | 7 | 36 |  |  |  |  | 1AAUDITORIUMTMY2 | 1A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 01:30,20/Mar | 67 | 10:30,25/Jul | 24 | 5C | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3909844 | 12:00, January | 3909844 | 12:00, January | 3909844 | 5C | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1097704 | 16:30, September | 244993
3A | TMY3 | 73 | 22 | 77 | 17 | 12 | 18 | 0 | 6 | 6 |  |  |  |  | 1AGYMTMY2 | 1A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,09/Feb | 58 | 04:30,07/Oct | 18 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY2 | 71 | 21 | 76 | 16 | 12 | 17 | 4 | 3 | 7 |  |  |  |  | 1AKITCHEN CAFETERIATMY2 | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 16:30,03/Jan | 63 | 04:30,23/Aug | 24 | 6A | Heating plant sensible load | 46 rooms | ROOMLOADS_TMY2.htg | Load (Btu/h) | 5063981 | 12:00, January | 5063981 | 12:00, January | 5063981 | 6A | Cooling plant sensible load | 46 rooms | ROOMLOADS_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1659937 | 14:30, September | 552584
3A | TMY15WA | 76 | 23 | 80 | 17 | 12 | 18 | 0 | 8 | 8 |  |  |  |  | 1AFLOOR 1TMY15WA | 1A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 6 | 18:30,09/Jan | 99 | 16:30,07/Oct | 88 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | MIN | 54 | 19 | 60 | 15 | 11 | 13 | 0 | 12 | 12 |  |  |  |  | 1AMECHTMY15WA | 1A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 01:30,04/Jan | 60 | 14:30,07/Oct | 33 | 6B | Heating plant sensible load | 46 rooms | ROOMLOAD_TMY2.htg | Load (Btu/h) | 5141729 | 12:00, January | 5141729 | 12:00, January | 5141729 | 6B | Cooling plant sensible load | 46 rooms | ROOMLOAD_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1535761 | 16:30, September | 413026
3A | MAX | 88 | 29 | 90 | 20 | 14 | 22 | 188 | 2 | 190 |  |  |  |  | 1AFLOOR 2TMY15WA | 1A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 31 | 07:30,09/Jan | 100 | 15:30,26/Mar | 94 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3B | TMY7WA | 16 | 20 | 17 | 17 | 16 | 16 | 15 | 13 | 28 | 3619627 | 2283118 |  |  | 1AAUDITORIUMTMY15WA | 1A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 03:30,03/Feb | 68 | 15:30,03/Jul | 28 | 7 | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 5145132 | 12:00, January | 5145132 | 12:00, January | 5145132 | 7 | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1362498 | 14:30, September | 385377
3B | TMY3WA | 17 | 21 | 18 | 18 | 16 | 17 | 10 | 16 | 26 |  |  |  |  | 1AGYMTMY15WA | 1A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,28/Dec | 59 | 04:30,25/Sep | 20 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3B | TMY3 | 17 | 20 | 19 | 19 | 17 | 17 | 8 | 15 | 23 |  |  |  |  | 1AKITCHEN CAFETERIATMY15WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 17:30,04/Jan | 63 | 04:30,28/Oct | 27 | 8 | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 5939305 | 12:00, January | 5939305 | 12:00, January | 5939305 | 8 | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1242278 | 16:30, May | 294945
3B | TMY2 | 17 | 20 | 18 | 18 | 17 | 17 | 14 | 9 | 23 |  |  |  |  | 1AFLOOR 1MIN | 1A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 00:30,08/Mar | 99 | 16:30,08/Sep | 66
3B | TMY15WA | 17 | 20 | 18 | 18 | 16 | 17 | 10 | 16 | 26 |  |  |  |  | 1AMECHMIN | 1A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 07:30,06/Dec | 55 | 15:30,08/Sep | 23
3B | MIN | 15 | 21 | 16 | 20 | 19 | 17 | 0 | 23 | 23 |  |  |  |  | 1AFLOOR 2MIN | 1A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 6 | 16:30,24/Jan | 100 | 16:30,28/Apr | 81
3B | MAX | 18 | 21 | 19 | 18 | 17 | 17 | 115 | 0 | 115 |  |  |  |  | 1AAUDITORIUMMIN | 1A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 03:30,08/Apr | 67 | 09:30,25/Jul | 19
3C | TMY7WA | 56 | 7 | 62 | 8 | 7 | 8 | 6 | 2 | 8 | 3224919 | 1134247 |  |  | 1AGYMMIN | 1A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 10:30,20/Nov | 56 | 00:30,26/Jul | 14
3C | TMY3WA | 63 | 8 | 68 | 8 | 7 | 10 | 2 | 2 | 4 |  |  |  |  | 1AKITCHEN CAFETERIAMIN | 1A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 17:30,11/Jan | 62 | 00:30,14/Aug | 18
3C | TMY3 | 57 | 8 | 63 | 8 | 7 | 8 | 0 | 8 | 8 |  |  |  |  | 1AFLOOR 1MAX | 1A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 77 | 07:30,15/Jan | 100 | 15:30,01/Sep | 93
3C | TMY2 | 54 | 8 | 60 | 9 | 8 | 8 | 2 | 2 | 4 |  |  |  |  | 1AMECHMAX | 1A | People dissatisfied | MECH | MAX | Percentage (%) | 20 | 08:30,16/Jan | 63 | 14:30,03/Sep | 38
3C | TMY15WA | 58 | 8 | 64 | 8 | 7 | 9 | 0 | 5 | 5 |  |  |  |  | 1AFLOOR 2MAX | 1A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 85 | 01:30,18/Apr | 100 | 15:30,08/Mar | 96
3C | MIN | 44 | 11 | 51 | 10 | 8 | 7 | 0 | 22 | 22 |  |  |  |  | 1AAUDITORIUMMAX | 1A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 6 | 11:30,20/Dec | 68 | 16:30,15/Aug | 33
3C | MAX | 69 | 11 | 74 | 10 | 8 | 12 | 36 | 0 | 36 |  |  |  |  | 1AGYMMAX | 1A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 11:30,04/Dec | 61 | 02:30,17/Sep | 24
4A | TMY7WA | 16 | 23 | 18 | 17 | 12 | 15 | 106 | 159 | 265 | 4186155 | 1834987 |  |  | 1AKITCHEN CAFETERIAMAX | 1A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 6 | 14:30,19/Dec | 63 | 18:30,18/Jul | 30
4A | TMY3WA | 17 | 25 | 19 | 18 | 13 | 16 | 96 | 133 | 229 |  |  |  |  | 2ALocationFilename | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
4A | TMY3 | 16 | 23 | 18 | 17 | 12 | 15 | 11 | 196 | 207 |  |  |  |  | 2AFLOOR 1TMY7WA | 2A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 19 | 05:30,18/Jan | 100 | 16:30,13/Sep | 85
4A | TMY2 | 16 | 22 | 18 | 17 | 12 | 15 | 25 | 122 | 147 |  |  |  |  | 2AMECHTMY7WA | 2A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 07:30,22/Jan | 56 | 14:30,28/May | 27
4A | TMY15WA | 17 | 25 | 19 | 18 | 13 | 16 | 26 | 192 | 218 |  |  |  |  | 2AFLOOR 2TMY7WA | 2A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 23 | 05:30,27/Dec | 100 | 15:30,09/Apr | 87
4A | MIN | 15 | 18 | 16 | 16 | 11 | 13 | 1 | 173 | 174 |  |  |  |  | 2AAUDITORIUMTMY7WA | 2A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 11:30,27/Dec | 69 | 16:30,18/Jul | 21
4A | MAX | 20 | 34 | 22 | 20 | 15 | 20 | 371 | 109 | 480 |  |  |  |  | 2AGYMTMY7WA | 2A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 11:30,27/Feb | 56 | 00:30,16/Aug | 15
4B | TMY7WA | 14 | 21 | 16 | 15 | 15 | 12 | 131 | 1219 | 1350 | 3979020 | 1620069 |  |  | 2AKITCHEN CAFETERIATMY7WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 11:30,16/Jan | 63 | 05:30,21/Aug | 22
4B | TMY3WA | 13 | 23 | 16 | 14 | 16 | 12 | 112 | 1270 | 1382 |  |  |  |  | 2AFLOOR 1TMY3WA | 2A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 8 | 05:30,21/Dec | 100 | 16:30,28/Sep | 88
4B | TMY3 | 14 | 23 | 16 | 15 | 15 | 13 | 59 | 1758 | 1817 |  |  |  |  | 2AMECHTMY3WA | 2A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 08:30,19/Jan | 61 | 15:30,20/Sep | 29
4B | TMY2 | 14 | 22 | 16 | 15 | 15 | 13 | 118 | 1490 | 1608 |  |  |  |  | 2AFLOOR 2TMY3WA | 2A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 8 | 06:30,20/Dec | 100 | 15:30,11/May | 90
4B | TMY15WA | 14 | 23 | 16 | 15 | 16 | 12 | 122 | 1754 | 1876 |  |  |  |  | 2AAUDITORIUMTMY3WA | 2A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 05:30,21/Feb | 67 | 11:30,18/Jul | 23
4B | MIN | 15 | 19 | 16 | 16 | 12 | 12 | 14 | 2341 | 2355 |  |  |  |  | 2AGYMTMY3WA | 2A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 11:30,07/Feb | 58 | 03:30,28/Sep | 16
4B | MAX | 14 | 27 | 16 | 15 | 20 | 13 | 539 | 484 | 1023 |  |  |  |  | 2AKITCHEN CAFETERIATMY3WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 12:30,25/Dec | 63 | 05:30,07/Jul | 24
4C | TMY7WA | 11 | 14 | 13 | 12 | 10 | 10 | 46 | 118 | 164 | 3717431 | 1703772 |  |  | 2AFLOOR 1TMY3 | 2A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 18 | 05:30,15/Feb | 100 | 15:30,03/Aug | 82
4C | TMY3WA | 10 | 12 | 12 | 11 | 9 | 9 | 44 | 57 | 101 |  |  |  |  | 2AMECHTMY3 | 2A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 21:30,09/Jan | 51 | 14:30,21/Sep | 25
4C | TMY3 | 11 | 13 | 13 | 11 | 9 | 10 | 16 | 218 | 234 |  |  |  |  | 2AFLOOR 2TMY3 | 2A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 16 | 06:30,12/Feb | 100 | 16:30,11/May | 85
4C | TMY2 | 11 | 13 | 13 | 11 | 9 | 10 | 52 | 315 | 367 |  |  |  |  | 2AAUDITORIUMTMY3 | 2A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 01:30,17/Mar | 67 | 10:30,25/Jul | 20
4C | TMY15WA | 11 | 13 | 13 | 11 | 10 | 9 | 28 | 287 | 315 |  |  |  |  | 2AGYMTMY3 | 2A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 09:30,20/Mar | 53 | 21:30,01/Aug | 14
4C | MIN | 14 | 16 | 15 | 15 | 10 | 9 | 0 | 866 | 866 |  |  |  |  | 2AKITCHEN CAFETERIATMY3 | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 11:30,02/Jan | 64 | 07:30,04/Jul | 21
4C | MAX | 12 | 18 | 14 | 12 | 12 | 12 | 386 | 1 | 387 |  |  |  |  | 2AFLOOR 1TMY2 | 2A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 10 | 06:30,14/Jan | 100 | 16:30,16/Sep | 81
5A | 5A_TMY7_WA | 15 | 21 | 17 | 16 | 11 | 14 | 208 | 89 | 297 | 4783322 | 1715606 |  |  | 2AMECHTMY2 | 2A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 08:30,23/Dec | 50 | 14:30,24/Sep | 25
5A | 5A_TMY3_WA | 15 | 21 | 17 | 16 | 11 | 14 | 219 | 76 | 295 |  |  |  |  | 2AFLOOR 2TMY2 | 2A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 8 | 06:30,11/Jan | 100 | 14:30,18/May | 84
5A | 5A_TMY3 | 15 | 21 | 17 | 16 | 11 | 14 | 51 | 83 | 134 |  |  |  |  | 2AAUDITORIUMTMY2 | 2A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 12:30,01/Feb | 67 | 10:30,17/Jul | 20
5A | 5A_TMY2 | 15 | 20 | 17 | 16 | 11 | 14 | 100 | 66 | 166 |  |  |  |  | 2AGYMTMY2 | 2A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 10:30,09/Jan | 51 | 04:30,05/Jul | 13
5A | 5A_TMY15_WA | 15 | 22 | 17 | 16 | 11 | 14 | 98 | 84 | 182 |  |  |  |  | 2AKITCHEN CAFETERIATMY2 | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 20:30,12/Jan | 64 | 07:30,11/Jul | 21
5A | 5A_MIN_WA | 16 | 19 | 16 | 16 | 11 | 12 | 5 | 154 | 159 |  |  |  |  | 2AFLOOR 1TMY15WA | 2A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 27 | 05:30,30/Dec | 100 | 16:30,13/Sep | 86
5A | 5A_MAX_WA | 17 | 26 | 19 | 17 | 12 | 17 | 785 | 9 | 794 |  |  |  |  | 2AMECHTMY15WA | 2A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 05:30,08/Mar | 56 | 14:30,14/Sep | 27
5B | TMY7WA | 14 | 17 | 15 | 15 | 12 | 11 | 265 | 1057 | 1322 | 4593129 | 1623303 |  |  | 2AFLOOR 2TMY15WA | 2A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 23 | 05:30,27/Dec | 100 | 12:30,29/Apr | 88
5B | TMY3WA | 13 | 17 | 15 | 14 | 12 | 11 | 231 | 1077 | 1308 |  |  |  |  | 2AAUDITORIUMTMY15WA | 2A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 11:30,27/Dec | 68 | 08:30,06/Jun | 21
5B | TMY3 | 14 | 19 | 15 | 14 | 14 | 12 | 230 | 839 | 1069 |  |  |  |  | 2AGYMTMY15WA | 2A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 13:30,10/Jan | 56 | 00:30,16/Aug | 15
5B | TMY2 | 14 | 19 | 15 | 15 | 13 | 12 | 295 | 867 | 1162 |  |  |  |  | 2AKITCHEN CAFETERIATMY15WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 13:30,11/Dec | 66 | 07:30,06/Jun | 23
5B | TMY15WA | 13 | 17 | 15 | 14 | 12 | 11 | 237 | 914 | 1151 |  |  |  |  | 2AFLOOR 1MIN | 2A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 7 | 17:30,18/Jan | 99 | 16:30,29/Jul | 63
5B | MIN | 18 | 21 | 18 | 18 | 13 | 13 | 73 | 1689 | 1762 |  |  |  |  | 2AMECHMIN | 2A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 04:30,19/Apr | 48 | 16:30,09/Sep | 21
5B | MAX | 13 | 20 | 15 | 13 | 14 | 11 | 1333 | 85 | 1418 |  |  |  |  | 2AFLOOR 2MIN | 2A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 7 | 17:30,13/Feb | 100 | 15:30,14/Jun | 69
5C | TMY7WA | 11 | 12 | 12 | 11 | 9 | 8 | 54 | 9 | 63 | 3909844 | 1097704 |  |  | 2AAUDITORIUMMIN | 2A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 12:30,19/Jan | 67 | 18:30,18/Jul | 18
5C | TMY3WA | 10 | 11 | 12 | 11 | 9 | 9 | 56 | 9 | 65 |  |  |  |  | 2AGYMMIN | 2A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 12:30,30/Oct | 48 | 19:30,13/Jun | 12
5C | TMY2 | 15 | 19 | 17 | 16 | 11 | 13 | 10 | 115 | 125 |  |  |  |  | 2AKITCHEN CAFETERIAMIN | 2A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 18:30,16/Feb | 61 | 22:30,08/Aug | 16
5C | TMY15WA | 10 | 11 | 12 | 11 | 9 | 8 | 33 | 32 | 65 |  |  |  |  | 2AFLOOR 1MAX | 2A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 72 | 00:30,18/Jan | 100 | 13:30,01/Sep | 94
5C | MIN | 14 | 16 | 14 | 15 | 10 | 9 | 16 | 29 | 45 |  |  |  |  | 2AMECHMAX | 2A | People dissatisfied | MECH | MAX | Percentage (%) | 10 | 00:30,18/Jan | 70 | 15:30,03/Sep | 35
5C | MAX | 10 | 13 | 13 | 11 | 9 | 10 | 0 | 356 | 356 |  |  |  |  | 2AFLOOR 2MAX | 2A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 70 | 00:30,18/Jan | 100 | 14:30,29/Mar | 95
5C | doeCWEC | 11 | 12 | 12 | 11 | 9 | 9 | 365 | 0 | 365 |  |  |  |  | 2AAUDITORIUMMAX | 2A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 6 | 10:30,15/Jan | 67 | 13:30,08/Aug | 28
5C | CWEC | 11 | 12 | 12 | 11 | 9 | 9 | 491 | 96 | 587 | 5063981 | 1659937 |  |  | 2AGYMMAX | 2A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 12:30,07/Feb | 59 | 03:30,28/Sep | 19
6A | TMY7WA | 15 | 21 | 17 | 16 | 11 | 14 | 404 | 150 | 554 |  |  |  |  | 2AKITCHEN CAFETERIAMAX | 2A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 6 | 09:30,25/Dec | 63 | 04:30,12/Jun | 27
6A | TMY3WA | 15 | 21 | 17 | 16 | 11 | 14 | 106 | 195 | 301 |  |  |  |  | 2BLocationFilename | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
6A | TMY3 | 16 | 21 | 18 | 17 | 12 | 14 | 335 | 181 | 516 |  |  |  |  | 2BFLOOR 1TMY7WA | 2B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,11/Mar | 58 | 02:30,23/Aug | 17
6A | TMY2 | 16 | 21 | 18 | 16 | 12 | 14 | 278 | 260 | 538 |  |  |  |  | 2BMECHTMY7WA | 2B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 22:30,14/Dec | 51 | 13:30,02/Sep | 21
6A | TMY15WA | 15 | 22 | 17 | 16 | 12 | 14 | 32 | 449 | 481 |  |  |  |  | 2BFLOOR 2TMY7WA | 2B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,02/Dec | 59 | 14:30,28/Aug | 19
6A | MIN | 17 | 21 | 18 | 17 | 12 | 13 | 1079 | 92 | 1171 |  |  |  |  | 2BAUDITORIUMTMY7WA | 2B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 21:30,19/Jan | 62 | 13:30,01/Aug | 17
6A | MAX | 18 | 29 | 20 | 18 | 14 | 17 | 426 | 686 | 1112 | 5141729 | 1535761 |  |  | 2BGYMTMY7WA | 2B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 10:30,02/Jan | 53 | 21:30,15/Aug | 14
6B | TMY7WA | 36 | 65 | 37 | 37 | 22 | 38 | 344 | 645 | 989 |  |  |  |  | 2BKITCHEN CAFETERIATMY7WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 08:30,26/Jan | 58 | 06:30,11/Jul | 16
6B | TMY3WA | 14 | 18 | 15 | 15 | 13 | 11 | 214 | 947 | 1161 |  |  |  |  | 2BFLOOR 1TMY3WA | 2B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 06:30,25/Nov | 55 | 14:30,25/Jul | 19
6B | TMY3 | 13 | 18 | 15 | 14 | 12 | 11 | 0 | 2153 | 2153 |  |  |  |  | 2BMECHTMY3WA | 2B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 01:30,18/Feb | 52 | 13:30,09/Sep | 23
6B | TMY2 | 14 | 18 | 15 | 15 | 12 | 11 | 242 | 797 | 1039 |  |  |  |  | 2BFLOOR 2TMY3WA | 2B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 06:30,12/Nov | 57 | 15:30,22/Aug | 20
6B | TMY15WA | 13 | 17 | 15 | 14 | 12 | 10 | 97 | 1513 | 1610 |  |  |  |  | 2BAUDITORIUMTMY3WA | 2B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 02:30,22/Feb | 61 | 13:30,15/Aug | 19
6B | MIN | 18 | 23 | 19 | 19 | 13 | 14 | 1388 | 81 | 1469 |  |  |  |  | 2BGYMTMY3WA | 2B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 16:30,18/Dec | 54 | 07:30,15/Aug | 15
6B | MAX | 13 | 20 | 15 | 14 | 15 | 11 | 681 | 64 | 745 | 5145132 | 1362498 |  |  | 2BKITCHEN CAFETERIATMY3WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 20:30,03/Dec | 57 | 05:30,15/Aug | 18
7 | TMY7WA | 15 | 19 | 16 | 15 | 11 | 13 | 613 | 65 | 678 |  |  |  |  | 2BFLOOR 1TMY3 | 2B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 06:30,11/Nov | 59 | 04:30,21/Jul | 20
7 | TMY3WA | 14 | 18 | 16 | 15 | 11 | 12 | 198 | 152 | 350 |  |  |  |  | 2BMECHTMY3 | 2B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 09:30,22/Dec | 52 | 13:30,03/Sep | 23
7 | TMY3 | 15 | 19 | 16 | 16 | 11 | 12 | 407 | 145 | 552 |  |  |  |  | 2BFLOOR 2TMY3 | 2B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 06:30,28/Oct | 58 | 04:30,21/Jul | 22
7 | TMY2 | 15 | 19 | 16 | 16 | 11 | 12 | 290 | 103 | 393 |  |  |  |  | 2BAUDITORIUMTMY3 | 2B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 00:30,23/Mar | 64 | 14:30,18/Jul | 20
7 | TMY15WA | 14 | 18 | 16 | 15 | 11 | 13 | 52 | 281 | 333 |  |  |  |  | 2BGYMTMY3 | 2B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,08/Mar | 55 | 06:30,18/Jul | 16
7 | MIN | 17 | 21 | 18 | 18 | 12 | 13 | 1211 | 25 | 1236 |  |  |  |  | 2BKITCHEN CAFETERIATMY3 | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 10:30,17/Jan | 57 | 06:30,15/Aug | 18
7 | MAX | 16 | 24 | 18 | 16 | 12 | 15 | 1316 | 97 | 1413 | 5939305 | 1242278 |  |  | 2BFLOOR 1TMY2 | 2B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 06:30,22/Apr | 54 | 09:30,03/Jul | 19
8 | TMY7WA | 16 | 20 | 17 | 16 | 12 | 13 | 1175 | 163 | 1338 |  |  |  |  | 2BMECHTMY2 | 2B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 01:30,14/Feb | 49 | 14:30,10/Sep | 22
8 | TMY3WA | 15 | 20 | 17 | 16 | 12 | 12 | 671 | 450 | 1121 |  |  |  |  | 2BFLOOR 2TMY2 | 2B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 06:30,28/Jan | 59 | 13:30,12/Sep | 21
8 | TMY3 | 16 | 21 | 18 | 17 | 12 | 14 | 955 | 259 | 1214 |  |  |  |  | 2BAUDITORIUMTMY2 | 2B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 20:30,11/Dec | 61 | 12:30,18/Jul | 19
8 | TMY2 | 17 | 21 | 18 | 18 | 12 | 14 | 873 | 445 | 1318 |  |  |  |  | 2BGYMTMY2 | 2B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,26/Nov | 55 | 19:30,11/Jul | 15
8 | TMY15WA | 16 | 20 | 17 | 16 | 12 | 13 | 224 | 955 | 1179 |  |  |  |  | 2BKITCHEN CAFETERIATMY2 | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 19:30,20/Jan | 54 | 05:30,30/Aug | 17
8 | MIN | 21 | 26 | 21 | 22 | 14 | 16 | 1904 | 0 | 1904 |  |  |  |  | 2BFLOOR 1TMY15WA | 2B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,15/Apr | 55 | 04:30,02/Aug | 18
8 | MAX | 15 | 20 | 17 | 15 | 14 | 12 | 1904 | 0 | 1904 |  |  |  |  | 2BMECHTMY15WA | 2B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 23:30,08/Dec | 51 | 14:30,06/Sep | 22
[15 empty] | 2BFLOOR 2TMY15WA | 2B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 06:30,02/Nov | 58 | 14:30,15/Aug | 20
[15 empty] | 2BAUDITORIUMTMY15WA | 2B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 08:30,20/Nov | 60 | 18:30,01/Aug | 18
[15 empty] | 2BGYMTMY15WA | 2B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 16:30,31/Jan | 53 | 19:30,25/Jul | 15
[15 empty] | 2BKITCHEN CAFETERIATMY15WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 14:30,19/Dec | 56 | 04:30,26/Jul | 17
[15 empty] | 2BFLOOR 1MIN | 2B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 08:30,20/Apr | 53 | 12:30,11/Jul | 16
[15 empty] | 2BMECHMIN | 2B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 08:30,19/Apr | 46 | 14:30,06/Sep | 18
[15 empty] | 2BFLOOR 2MIN | 2B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 06:30,08/Jun | 56 | 14:30,11/Jul | 17
[15 empty] | 2BAUDITORIUMMIN | 2B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 18:30,11/Jan | 59 | 15:30,24/Jul | 15
[15 empty] | 2BGYMMIN | 2B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 12:30,03/Feb | 42 | 05:30,20/Jul | 12
[15 empty] | 2BKITCHEN CAFETERIAMIN | 2B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 18:30,20/Jan | 54 | 05:30,20/Jul | 13
[15 empty] | 2BFLOOR 1MAX | 2B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 06:30,10/Feb | 55 | 16:30,25/Jul | 20
[15 empty] | 2BMECHMAX | 2B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 20:30,19/Dec | 55 | 14:30,08/Sep | 25
[15 empty] | 2BFLOOR 2MAX | 2B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,01/Feb | 58 | 12:30,04/Sep | 21
[15 empty] | 2BAUDITORIUMMAX | 2B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 02:30,26/Jan | 59 | 14:30,11/Jul | 20
[15 empty] | 2BGYMMAX | 2B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 08:30,29/Dec | 56 | 05:30,02/Sep | 17
[15 empty] | 2BKITCHEN CAFETERIAMAX | 2B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 08:30,17/Dec | 53 | 23:30,24/Aug | 19
[15 empty] | 3ALocationFilename | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 3AFLOOR 1TMY7WA | 3A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 9 | 06:30,04/Jan | 99 | 16:30,12/Jul | 74
[15 empty] | 3AMECHTMY7WA | 3A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 09:30,20/Feb | 54 | 14:30,06/Sep | 22
[15 empty] | 3AFLOOR 2TMY7WA | 3A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 10 | 06:30,04/Jan | 100 | 16:30,06/May | 78
[15 empty] | 3AAUDITORIUMTMY7WA | 3A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 14:30,07/Dec | 65 | 11:30,14/Aug | 17
[15 empty] | 3AGYMTMY7WA | 3A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 14:30,04/Dec | 52 | 01:30,26/Jul | 12
[15 empty] | 3AKITCHEN CAFETERIATMY7WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 12:30,12/Dec | 62 | 02:30,16/Aug | 17
[15 empty] | 3AFLOOR 1TMY3WA | 3A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 21 | 06:30,27/Feb | 99 | 15:30,26/Jul | 78
[15 empty] | 3AMECHTMY3WA | 3A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 01:30,04/Mar | 51 | 14:30,19/May | 23
[15 empty] | 3AFLOOR 2TMY3WA | 3A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 20 | 05:30,25/Feb | 100 | 14:30,13/May | 82
[15 empty] | 3AAUDITORIUMTMY3WA | 3A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 12:30,19/Jan | 65 | 11:30,14/Aug | 17
[15 empty] | 3AGYMTMY3WA | 3A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 14:30,17/Jan | 47 | 20:30,27/Jun | 12
[15 empty] | 3AKITCHEN CAFETERIATMY3WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 13:30,27/Feb | 64 | 23:30,18/Jul | 18
[15 empty] | 3AFLOOR 1TMY3 | 3A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 7 | 06:30,15/Feb | 99 | 13:30,09/Sep | 73
[15 empty] | 3AMECHTMY3 | 3A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 03:30,07/Mar | 49 | 14:30,09/Sep | 22
[15 empty] | 3AFLOOR 2TMY3 | 3A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 7 | 16:30,14/Feb | 100 | 16:30,06/Jul | 77
[15 empty] | 3AAUDITORIUMTMY3 | 3A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 11:30,28/Dec | 63 | 14:30,01/Aug | 17
[15 empty] | 3AGYMTMY3 | 3A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 10:30,11/Jan | 44 | 20:30,13/Jun | 12
[15 empty] | 3AKITCHEN CAFETERIATMY3 | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 17:30,26/Jan | 60 | 03:30,09/Aug | 18
[15 empty] | 3AFLOOR 1TMY2 | 3A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 8 | 07:30,18/Jan | 98 | 17:30,02/Jul | 71
[15 empty] | 3AMECHTMY2 | 3A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 08:30,08/Nov | 46 | 14:30,14/May | 21
[15 empty] | 3AFLOOR 2TMY2 | 3A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 8 | 05:30,19/Jan | 100 | 15:30,02/Jul | 76
[15 empty] | 3AAUDITORIUMTMY2 | 3A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 04:30,28/Oct | 64 | 12:30,25/Jul | 16
[15 empty] | 3AGYMTMY2 | 3A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 14:30,22/Dec | 44 | 21:30,03/Jul | 12
[15 empty] | 3AKITCHEN CAFETERIATMY2 | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 20:30,29/Jan | 58 | 06:30,04/Jul | 17
[15 empty] | 3AFLOOR 1TMY15WA | 3A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 20 | 06:30,07/Feb | 99 | 16:30,12/Jul | 76
[15 empty] | 3AMECHTMY15WA | 3A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 08:30,03/Mar | 51 | 15:30,07/Sep | 23
[15 empty] | 3AFLOOR 2TMY15WA | 3A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 16 | 05:30,02/Feb | 100 | 16:30,20/May | 80
[15 empty] | 3AAUDITORIUMTMY15WA | 3A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 12:30,19/Jan | 65 | 11:30,14/Aug | 17
[15 empty] | 3AGYMTMY15WA | 3A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 14:30,17/Jan | 52 | 01:30,26/Jul | 12
[15 empty] | 3AKITCHEN CAFETERIATMY15WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 15:30,24/Jan | 62 | 02:30,16/Aug | 18
[15 empty] | 3AFLOOR 1MIN | 3A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 7 | 07:30,22/Feb | 97 | 16:30,09/Aug | 54
[15 empty] | 3AMECHMIN | 3A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 02:30,03/May | 44 | 16:30,10/Sep | 19
[15 empty] | 3AFLOOR 2MIN | 3A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 8 | 17:30,07/Mar | 100 | 16:30,10/Sep | 60
[15 empty] | 3AAUDITORIUMMIN | 3A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 14:30,29/Oct | 57 | 16:30,29/Aug | 15
[15 empty] | 3AGYMMIN | 3A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 13:30,03/Feb | 40 | 06:30,24/Jan | 11
[15 empty] | 3AKITCHEN CAFETERIAMIN | 3A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 13:30,18/Jan | 49 | 22:30,11/Jul | 13
[15 empty] | 3AFLOOR 1MAX | 3A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 46 | 05:30,27/Dec | 100 | 15:30,30/Jun | 88
[15 empty] | 3AMECHMAX | 3A | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 01:30,25/Jan | 55 | 17:30,07/Sep | 29
[15 empty] | 3AFLOOR 2MAX | 3A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 42 | 07:30,07/Feb | 100 | 16:30,29/Apr | 90
[15 empty] | 3AAUDITORIUMMAX | 3A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 08:30,03/Jan | 64 | 13:30,08/Aug | 20
[15 empty] | 3AGYMMAX | 3A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 14:30,25/Dec | 53 | 01:30,26/Jul | 14
[15 empty] | 3AKITCHEN CAFETERIAMAX | 3A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 08:30,08/Feb | 61 | 01:30,30/Aug | 22
[15 empty] | 3BLocationFilename | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 3BFLOOR 1TMY7WA | 3B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 07:30,22/Mar | 51 | 14:30,25/Jul | 16
[15 empty] | 3BMECHTMY7WA | 3B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 01:30,13/Mar | 49 | 13:30,17/Sep | 20
[15 empty] | 3BFLOOR 2TMY7WA | 3B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 06:30,22/Oct | 53 | 11:30,11/Jul | 17
[15 empty] | 3BAUDITORIUMTMY7WA | 3B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 04:30,18/Apr | 56 | 09:30,11/Jul | 17
[15 empty] | 3BGYMTMY7WA | 3B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 09:30,13/Nov | 60 | 05:30,20/Dec | 16
[15 empty] | 3BKITCHEN CAFETERIATMY7WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 15:30,27/Dec | 55 | 07:30,11/Jul | 16
[15 empty] | 3BFLOOR 1TMY3WA | 3B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,28/Oct | 52 | 08:30,22/Aug | 17
[15 empty] | 3BMECHTMY3WA | 3B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 00:30,25/Feb | 49 | 13:30,17/Sep | 21
[15 empty] | 3BFLOOR 2TMY3WA | 3B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,18/Mar | 56 | 13:30,07/Aug | 18
[15 empty] | 3BAUDITORIUMTMY3WA | 3B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 08:30,30/Mar | 57 | 14:30,22/Aug | 18
[15 empty] | 3BGYMTMY3WA | 3B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 09:30,13/Nov | 61 | 05:30,06/Dec | 16
[15 empty] | 3BKITCHEN CAFETERIATMY3WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 15:30,07/Jan | 55 | 06:30,01/Aug | 17
[15 empty] | 3BFLOOR 1TMY3 | 3B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 06:30,02/Apr | 53 | 01:30,01/Aug | 17
[15 empty] | 3BMECHTMY3 | 3B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 09:30,29/Mar | 51 | 14:30,02/Sep | 20
[15 empty] | 3BFLOOR 2TMY3 | 3B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,15/Apr | 55 | 12:30,07/Aug | 19
[15 empty] | 3BAUDITORIUMTMY3 | 3B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 20:30,03/Feb | 59 | 12:30,07/Aug | 19
[15 empty] | 3BGYMTMY3 | 3B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,06/Nov | 55 | 06:30,13/Dec | 17
[15 empty] | 3BKITCHEN CAFETERIATMY3 | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 14:30,15/Feb | 54 | 06:30,07/Aug | 17
[15 empty] | 3BFLOOR 1TMY2 | 3B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 06:30,06/Apr | 51 | 14:30,11/Jul | 17
[15 empty] | 3BMECHTMY2 | 3B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 01:30,26/Mar | 52 | 06:30,11/Jan | 20
[15 empty] | 3BFLOOR 2TMY2 | 3B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 06:30,02/Apr | 55 | 13:30,07/Aug | 18
[15 empty] | 3BAUDITORIUMTMY2 | 3B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 10:30,08/Feb | 67 | 06:30,11/Jan | 18
[15 empty] | 3BGYMTMY2 | 3B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 09:30,25/Feb | 69 | 06:30,11/Jan | 17
[15 empty] | 3BKITCHEN CAFETERIATMY2 | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 17:30,12/Mar | 54 | 06:30,07/Aug | 17
[15 empty] | 3BFLOOR 1TMY15WA | 3B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,05/Apr | 53 | 00:30,02/Aug | 17
[15 empty] | 3BMECHTMY15WA | 3B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 08:30,15/Apr | 50 | 14:30,03/Sep | 20
[15 empty] | 3BFLOOR 2TMY15WA | 3B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,18/Mar | 53 | 11:30,11/Jul | 18
[15 empty] | 3BAUDITORIUMTMY15WA | 3B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 00:30,16/Mar | 56 | 09:30,11/Jul | 18
[15 empty] | 3BGYMTMY15WA | 3B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,13/Nov | 61 | 05:30,06/Dec | 16
[15 empty] | 3BKITCHEN CAFETERIATMY15WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 15:30,23/Dec | 55 | 07:30,11/Jul | 17
[15 empty] | 3BFLOOR 1MIN | 3B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 06:30,20/May | 45 | 14:30,31/Jul | 15
[15 empty] | 3BMECHMIN | 3B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 01:30,12/May | 66 | 05:30,18/Jan | 21
[15 empty] | 3BFLOOR 2MIN | 3B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 06:30,31/Aug | 52 | 14:30,22/Aug | 16
[15 empty] | 3BAUDITORIUMMIN | 3B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 08:30,29/May | 79 | 07:30,17/Jan | 20
[15 empty] | 3BGYMMIN | 3B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 15:30,08/May | 80 | 05:30,18/Jan | 19
[15 empty] | 3BKITCHEN CAFETERIAMIN | 3B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 14:30,02/Dec | 58 | 15:30,17/Jan | 17
[15 empty] | 3BFLOOR 1MAX | 3B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 06:30,12/Mar | 51 | 13:30,05/Sep | 18
[15 empty] | 3BMECHMAX | 3B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 01:30,23/Jan | 54 | 14:30,03/Sep | 21
[15 empty] | 3BFLOOR 2MAX | 3B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,10/Nov | 56 | 12:30,05/Sep | 19
[15 empty] | 3BAUDITORIUMMAX | 3B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 00:30,01/Dec | 59 | 14:30,05/Sep | 18
[15 empty] | 3BGYMMAX | 3B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 11:30,20/Nov | 52 | 04:30,24/Jul | 17
[15 empty] | 3BKITCHEN CAFETERIAMAX | 3B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 16:30,27/Dec | 53 | 01:30,27/Jul | 17
[15 empty] | 3CLocationFilename | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 3CFLOOR 1TMY7WA | 3C | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 22 | 05:30,11/Jan | 88 | 14:30,14/Oct | 56
[15 empty] | 3CMECHTMY7WA | 3C | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 02:30,01/Sep | 31 | 06:30,11/Jan | 7
[15 empty] | 3CFLOOR 2TMY7WA | 3C | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 23 | 07:30,10/Jan | 98 | 14:30,14/Oct | 62
[15 empty] | 3CAUDITORIUMTMY7WA | 3C | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 09:30,12/Jan | 26 | 03:30,11/Jan | 8
[15 empty] | 3CGYMTMY7WA | 3C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 13:30,21/Mar | 27 | 07:30,10/Jan | 7
[15 empty] | 3CKITCHEN CAFETERIATMY7WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 20:30,11/Jan | 25 | 10:30,14/Oct | 8
[15 empty] | 3CFLOOR 1TMY3WA | 3C | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 25 | 05:30,09/Feb | 92 | 14:30,05/Oct | 63
[15 empty] | 3CMECHTMY3WA | 3C | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 23:30,30/Jul | 27 | 14:30,05/Oct | 8
[15 empty] | 3CFLOOR 2TMY3WA | 3C | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 23 | 05:30,09/Feb | 98 | 14:30,23/Sep | 68
[15 empty] | 3CAUDITORIUMTMY3WA | 3C | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 14:30,30/Mar | 31 | 15:30,03/Oct | 8
[15 empty] | 3CGYMTMY3WA | 3C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 09:30,25/Dec | 22 | 05:30,08/Feb | 7
[15 empty] | 3CKITCHEN CAFETERIATMY3WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 19:30,30/Dec | 29 | 06:30,25/Sep | 10
[15 empty] | 3CFLOOR 1TMY3 | 3C | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 24 | 05:30,11/Jan | 89 | 14:30,24/Sep | 57
[15 empty] | 3CMECHTMY3 | 3C | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 23:30,22/May | 31 | 06:30,11/Jan | 8
[15 empty] | 3CFLOOR 2TMY3 | 3C | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 23 | 07:30,26/Dec | 98 | 15:30,15/Sep | 63
[15 empty] | 3CAUDITORIUMTMY3 | 3C | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 04:30,27/Sep | 25 | 05:30,27/Dec | 8
[15 empty] | 3CGYMTMY3 | 3C | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 09:30,18/Dec | 26 | 05:30,27/Dec | 7
[15 empty] | 3CKITCHEN CAFETERIATMY3 | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 12:30,25/Dec | 23 | 10:30,12/May | 8
[15 empty] | 3CFLOOR 1TMY2 | 3C | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 22 | 05:30,26/Dec | 92 | 14:30,30/Sep | 54
[15 empty] | 3CMECHTMY2 | 3C | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 00:30,13/Sep | 34 | 07:30,26/Dec | 8
[15 empty] | 3CFLOOR 2TMY2 | 3C | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 21 | 07:30,02/Jan | 98 | 16:30,28/Sep | 60
[15 empty] | 3CAUDITORIUMTMY2 | 3C | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 08:30,23/Mar | 36 | 14:30,03/Jul | 9
[15 empty] | 3CGYMTMY2 | 3C | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 13:30,20/Mar | 29 | 05:30,26/Dec | 8
[15 empty] | 3CKITCHEN CAFETERIATMY2 | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 09:30,10/Apr | 29 | 04:30,30/Sep | 8
[15 empty] | 3CFLOOR 1TMY15WA | 3C | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 28 | 07:30,25/Dec | 92 | 14:30,20/Sep | 58
[15 empty] | 3CMECHTMY15WA | 3C | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 01:30,10/Oct | 27 | 14:30,20/Sep | 8
[15 empty] | 3CFLOOR 2TMY15WA | 3C | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 28 | 05:30,20/Jan | 98 | 14:30,17/Sep | 64
[15 empty] | 3CAUDITORIUMTMY15WA | 3C | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 11:30,10/Mar | 41 | 14:30,19/Sep | 8
[15 empty] | 3CGYMTMY15WA | 3C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 15:30,17/Jan | 18 | 17:30,31/May | 7
[15 empty] | 3CKITCHEN CAFETERIATMY15WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 08:30,06/Dec | 29 | 19:30,19/Sep | 9
[15 empty] | 3CFLOOR 1MIN | 3C | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 20 | 05:30,13/Jan | 79 | 14:30,10/Sep | 44
[15 empty] | 3CMECHMIN | 3C | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 02:30,11/Sep | 37 | 04:30,13/Jan | 11
[15 empty] | 3CFLOOR 2MIN | 3C | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 20 | 05:30,13/Jan | 94 | 15:30,10/Sep | 51
[15 empty] | 3CAUDITORIUMMIN | 3C | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 14:30,15/Mar | 28 | 03:30,06/Dec | 10
[15 empty] | 3CGYMMIN | 3C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 13:30,12/Jun | 30 | 02:30,06/Dec | 8
[15 empty] | 3CKITCHEN CAFETERIAMIN | 3C | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 17:30,27/Jan | 19 | 13:30,09/Sep | 7
[15 empty] | 3CFLOOR 1MAX | 3C | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 39 | 23:30,03/Jan | 93 | 14:30,30/Sep | 69
[15 empty] | 3CMECHMAX | 3C | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 21:30,04/Dec | 30 | 14:30,13/Sep | 11
[15 empty] | 3CFLOOR 2MAX | 3C | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 38 | 00:30,04/Jan | 99 | 14:30,13/Sep | 74
[15 empty] | 3CAUDITORIUMMAX | 3C | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 07:30,18/Mar | 47 | 15:30,29/Aug | 10
[15 empty] | 3CGYMMAX | 3C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 15:30,14/Feb | 22 | 17:30,26/Oct | 8
[15 empty] | 3CKITCHEN CAFETERIAMAX | 3C | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 08:30,20/Jan | 36 | 19:30,29/Aug | 12
[15 empty] | 4ALocationFilename | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 4AFLOOR 1TMY7WA | 4A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 07:30,27/Oct | 60 | 08:30,25/Jul | 16
[15 empty] | 4AMECHTMY7WA | 4A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 00:30,17/Nov | 79 | 14:30,23/Jul | 23
[15 empty] | 4AFLOOR 2TMY7WA | 4A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,19/Oct | 58 | 09:30,25/Jul | 18
[15 empty] | 4AAUDITORIUMTMY7WA | 4A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 09:30,12/Jan | 63 | 12:30,25/Jul | 17
[15 empty] | 4AGYMTMY7WA | 4A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 14:30,05/Dec | 45 | 07:30,24/Jul | 12
[15 empty] | 4AKITCHEN CAFETERIATMY7WA | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 20:30,04/Mar | 60 | 07:30,25/Jul | 15
[15 empty] | 4AFLOOR 1TMY3WA | 4A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,04/May | 60 | 08:30,25/Jul | 17
[15 empty] | 4AMECHTMY3WA | 4A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 08:30,02/Apr | 79 | 14:30,23/Jul | 25
[15 empty] | 4AFLOOR 2TMY3WA | 4A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,31/Mar | 58 | 09:30,25/Jul | 19
[15 empty] | 4AAUDITORIUMTMY3WA | 4A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 15:30,11/Nov | 63 | 12:30,25/Jul | 18
[15 empty] | 4AGYMTMY3WA | 4A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 10:30,09/Jan | 47 | 17:30,30/Sep | 13
[15 empty] | 4AKITCHEN CAFETERIATMY3WA | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 20:30,28/Jan | 60 | 07:30,25/Jul | 16
[15 empty] | 4AFLOOR 1TMY3 | 4A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 06:30,22/Apr | 55 | 12:30,05/Sep | 16
[15 empty] | 4AMECHTMY3 | 4A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 00:30,02/May | 73 | 16:30,06/Sep | 23
[15 empty] | 4AFLOOR 2TMY3 | 4A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,20/Oct | 57 | 18:30,05/Sep | 18
[15 empty] | 4AAUDITORIUMTMY3 | 4A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 08:30,10/Apr | 64 | 13:30,05/Sep | 17
[15 empty] | 4AGYMTMY3 | 4A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,02/Nov | 44 | 20:30,11/Jul | 12
[15 empty] | 4AKITCHEN CAFETERIATMY3 | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 18:30,04/Feb | 56 | 07:30,11/Jul | 15
[15 empty] | 4AFLOOR 1TMY2 | 4A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,05/May | 55 | 10:30,25/Jul | 16
[15 empty] | 4AMECHTMY2 | 4A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 23:30,18/Oct | 68 | 16:30,09/Aug | 22
[15 empty] | 4AFLOOR 2TMY2 | 4A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,30/Apr | 59 | 09:30,25/Jul | 18
[15 empty] | 4AAUDITORIUMTMY2 | 4A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 20:30,14/Jan | 68 | 10:30,25/Jul | 17
[15 empty] | 4AGYMTMY2 | 4A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 10:30,09/Jan | 45 | 05:30,18/Jan | 12
[15 empty] | 4AKITCHEN CAFETERIATMY2 | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 20:30,22/Jan | 58 | 22:30,25/Jul | 15
[15 empty] | 4AFLOOR 1TMY15WA | 4A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,05/Nov | 60 | 08:30,25/Jul | 17
[15 empty] | 4AMECHTMY15WA | 4A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 06:30,02/Nov | 79 | 14:30,23/Jul | 25
[15 empty] | 4AFLOOR 2TMY15WA | 4A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,17/Mar | 58 | 09:30,25/Jul | 19
[15 empty] | 4AAUDITORIUMTMY15WA | 4A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 20:30,12/Feb | 63 | 12:30,25/Jul | 18
[15 empty] | 4AGYMTMY15WA | 4A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 12:30,28/Mar | 45 | 07:30,24/Jul | 13
[15 empty] | 4AKITCHEN CAFETERIATMY15WA | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 15:30,18/Apr | 60 | 07:30,25/Jul | 16
[15 empty] | 4AFLOOR 1MIN | 4A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,30/Sep | 39 | 07:30,24/Jan | 15
[15 empty] | 4AMECHMIN | 4A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 01:30,26/May | 42 | 16:30,08/Sep | 18
[15 empty] | 4AFLOOR 2MIN | 4A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,30/Sep | 52 | 18:30,01/Aug | 16
[15 empty] | 4AAUDITORIUMMIN | 4A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 08:30,12/Jun | 46 | 18:30,01/Aug | 16
[15 empty] | 4AGYMMIN | 4A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,14/Jan | 45 | 05:30,11/Jan | 11
[15 empty] | 4AKITCHEN CAFETERIAMIN | 4A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 13:30,06/Dec | 40 | 19:30,01/Aug | 13
[15 empty] | 4AFLOOR 1MAX | 4A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,12/Feb | 58 | 04:30,08/Aug | 20
[15 empty] | 4AMECHMAX | 4A | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 08:30,30/Jan | 84 | 18:30,31/May | 34
[15 empty] | 4AFLOOR 2MAX | 4A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,31/Mar | 61 | 14:30,31/Jul | 22
[15 empty] | 4AAUDITORIUMMAX | 4A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 07:30,29/Mar | 65 | 13:30,01/Aug | 20
[15 empty] | 4AGYMMAX | 4A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 15:30,26/Dec | 53 | 00:30,05/Jul | 15
[15 empty] | 4AKITCHEN CAFETERIAMAX | 4A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 13:30,14/Feb | 60 | 05:30,08/Aug | 20
[15 empty] | 4BLocationFilename | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 4BFLOOR 1TMY7WA | 4B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,17/May | 41 | 16:30,18/Jul | 14
[15 empty] | 4BMECHTMY7WA | 4B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 21:30,14/Apr | 77 | 14:30,20/Jul | 21
[15 empty] | 4BFLOOR 2TMY7WA | 4B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,22/Oct | 50 | 14:30,18/Jul | 16
[15 empty] | 4BAUDITORIUMTMY7WA | 4B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 14:30,12/Feb | 54 | 13:30,18/Jul | 15
[15 empty] | 4BGYMTMY7WA | 4B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 14:30,27/Jan | 62 | 18:30,02/Sep | 15
[15 empty] | 4BKITCHEN CAFETERIATMY7WA | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 12:30,14/Mar | 41 | 19:30,18/Jul | 12
[15 empty] | 4BFLOOR 1TMY3WA | 4B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,25/Mar | 41 | 14:30,01/Aug | 13
[15 empty] | 4BMECHTMY3WA | 4B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 01:30,04/Nov | 75 | 14:30,08/Sep | 23
[15 empty] | 4BFLOOR 2TMY3WA | 4B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 06:30,12/May | 54 | 12:30,11/Jul | 16
[15 empty] | 4BAUDITORIUMTMY3WA | 4B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 10:30,11/Apr | 56 | 13:30,11/Jul | 14
[15 empty] | 4BGYMTMY3WA | 4B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 12:30,14/Mar | 63 | 18:30,02/Sep | 16
[15 empty] | 4BKITCHEN CAFETERIATMY3WA | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 16:30,19/Jan | 39 | 07:30,01/Aug | 12
[15 empty] | 4BFLOOR 1TMY3 | 4B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 06:30,27/Apr | 44 | 15:30,25/Jul | 14
[15 empty] | 4BMECHTMY3 | 4B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 21:30,18/Apr | 73 | 14:30,29/Jun | 23
[15 empty] | 4BFLOOR 2TMY3 | 4B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,11/May | 52 | 15:30,21/Aug | 16
[15 empty] | 4BAUDITORIUMTMY3 | 4B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 11:30,19/Mar | 53 | 10:30,25/Jul | 15
[15 empty] | 4BGYMTMY3 | 4B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 16:30,11/Jan | 63 | 18:30,20/May | 15
[15 empty] | 4BKITCHEN CAFETERIATMY3 | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 20:30,01/Dec | 43 | 07:30,04/Jul | 13
[15 empty] | 4BFLOOR 1TMY2 | 4B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 06:30,20/Apr | 46 | 21:30,01/Aug | 14
[15 empty] | 4BMECHTMY2 | 4B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 09:30,18/Apr | 68 | 15:30,03/Sep | 22
[15 empty] | 4BFLOOR 2TMY2 | 4B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,12/Oct | 53 | 14:30,01/Aug | 16
[15 empty] | 4BAUDITORIUMTMY2 | 4B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 12:30,18/Mar | 54 | 15:30,01/Aug | 15
[15 empty] | 4BGYMTMY2 | 4B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 14:30,10/Apr | 64 | 19:30,20/May | 15
[15 empty] | 4BKITCHEN CAFETERIATMY2 | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 18:30,27/Jan | 49 | 22:30,01/Aug | 13
[15 empty] | 4BFLOOR 1TMY15WA | 4B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,27/Apr | 41 | 16:30,18/Jul | 14
[15 empty] | 4BMECHTMY15WA | 4B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 00:30,10/Apr | 77 | 14:30,20/Jul | 23
[15 empty] | 4BFLOOR 2TMY15WA | 4B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 06:30,12/May | 51 | 14:30,28/Aug | 16
[15 empty] | 4BAUDITORIUMTMY15WA | 4B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 11:30,03/Mar | 54 | 13:30,18/Jul | 15
[15 empty] | 4BGYMTMY15WA | 4B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 15:30,07/Nov | 61 | 18:30,24/Sep | 16
[15 empty] | 4BKITCHEN CAFETERIATMY15WA | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 14:30,23/Jan | 41 | 19:30,18/Jul | 12
[15 empty] | 4BFLOOR 1MIN | 4B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 06:30,16/Jun | 41 | 04:30,03/Feb | 15
[15 empty] | 4BMECHMIN | 4B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 00:30,22/May | 67 | 06:30,03/Feb | 19
[15 empty] | 4BFLOOR 2MIN | 4B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,04/Jun | 45 | 16:30,31/Jul | 16
[15 empty] | 4BAUDITORIUMMIN | 4B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 19:30,22/Feb | 47 | 03:30,03/Feb | 16
[15 empty] | 4BGYMMIN | 4B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 16:30,23/Mar | 57 | 19:30,31/May | 12
[15 empty] | 4BKITCHEN CAFETERIAMIN | 4B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 21:30,08/Oct | 40 | 20:30,02/Feb | 12
[15 empty] | 4BFLOOR 1MAX | 4B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,25/Mar | 43 | 18:30,18/Jul | 14
[15 empty] | 4BMECHMAX | 4B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 22:30,09/Nov | 80 | 18:30,31/May | 27
[15 empty] | 4BFLOOR 2MAX | 4B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,23/Apr | 52 | 13:30,29/Aug | 16
[15 empty] | 4BAUDITORIUMMAX | 4B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 11:30,02/Feb | 53 | 14:30,17/Jul | 15
[15 empty] | 4BGYMMAX | 4B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 14:30,06/Mar | 68 | 18:30,31/May | 20
[15 empty] | 4BKITCHEN CAFETERIAMAX | 4B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 19:30,15/Feb | 42 | 19:30,08/Aug | 13
[15 empty] | 4CLocationFilename | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 4CFLOOR 1TMY7WA | 4C | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,10/Jun | 40 | 15:30,01/Aug | 11
[15 empty] | 4CMECHTMY7WA | 4C | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 21:30,19/Jun | 64 | 16:30,10/Sep | 14
[15 empty] | 4CFLOOR 2TMY7WA | 4C | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,14/Oct | 53 | 14:30,01/Aug | 13
[15 empty] | 4CAUDITORIUMTMY7WA | 4C | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 15:30,12/Jan | 54 | 14:30,01/Aug | 12
[15 empty] | 4CGYMTMY7WA | 4C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 09:30,18/Jan | 50 | 17:30,07/May | 10
[15 empty] | 4CKITCHEN CAFETERIATMY7WA | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 12:30,24/Apr | 38 | 19:30,01/Aug | 10
[15 empty] | 4CFLOOR 1TMY3WA | 4C | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,04/Oct | 32 | 15:30,15/Aug | 10
[15 empty] | 4CMECHTMY3WA | 4C | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 14:30,06/Jun | 59 | 16:30,15/Sep | 12
[15 empty] | 4CFLOOR 2TMY3WA | 4C | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 06:30,13/Sep | 48 | 14:30,11/Jul | 12
[15 empty] | 4CAUDITORIUMTMY3WA | 4C | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 08:30,09/Nov | 43 | 16:30,14/Aug | 11
[15 empty] | 4CGYMTMY3WA | 4C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 09:30,21/Feb | 51 | 17:30,06/Sep | 9
[15 empty] | 4CKITCHEN CAFETERIATMY3WA | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 13:30,28/Feb | 29 | 18:30,15/Aug | 9
[15 empty] | 4CFLOOR 1TMY3 | 4C | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,15/Oct | 34 | 20:30,09/Sep | 11
[15 empty] | 4CMECHTMY3 | 4C | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 01:30,28/Oct | 52 | 16:30,10/Sep | 13
[15 empty] | 4CFLOOR 2TMY3 | 4C | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,06/Oct | 49 | 18:30,21/Jul | 13
[15 empty] | 4CAUDITORIUMTMY3 | 4C | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 02:30,08/Oct | 41 | 16:30,05/Jun | 11
[15 empty] | 4CGYMTMY3 | 4C | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 13:30,23/May | 48 | 19:30,05/Apr | 9
[15 empty] | 4CKITCHEN CAFETERIATMY3 | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 16:30,06/Dec | 35 | 19:30,08/Aug | 10
[15 empty] | 4CFLOOR 1TMY2 | 4C | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,09/Apr | 33 | 20:30,09/Sep | 11
[15 empty] | 4CMECHTMY2 | 4C | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 09:30,12/Jun | 52 | 17:30,10/Sep | 13
[15 empty] | 4CFLOOR 2TMY2 | 4C | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,04/Oct | 45 | 18:30,09/Sep | 13
[15 empty] | 4CAUDITORIUMTMY2 | 4C | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 15:30,11/Jan | 42 | 05:30,31/Jan | 11
[15 empty] | 4CGYMTMY2 | 4C | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 09:30,29/Jan | 56 | 19:30,17/May | 9
[15 empty] | 4CKITCHEN CAFETERIATMY2 | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 15:30,10/Apr | 35 | 20:30,15/Aug | 10
[15 empty] | 4CFLOOR 1TMY15WA | 4C | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,10/Jun | 40 | 15:30,01/Aug | 11
[15 empty] | 4CMECHTMY15WA | 4C | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 21:30,19/Jun | 64 | 16:30,10/Sep | 13
[15 empty] | 4CFLOOR 2TMY15WA | 4C | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,22/Apr | 53 | 14:30,01/Aug | 13
[15 empty] | 4CAUDITORIUMTMY15WA | 4C | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 12:30,08/Jan | 54 | 14:30,01/Aug | 11
[15 empty] | 4CGYMTMY15WA | 4C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 10:30,02/Dec | 49 | 17:30,07/Sep | 10
[15 empty] | 4CKITCHEN CAFETERIATMY15WA | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 13:30,13/Mar | 38 | 19:30,01/Aug | 9
[15 empty] | 4CFLOOR 1MIN | 4C | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,02/Jul | 35 | 07:30,07/Feb | 14
[15 empty] | 4CMECHMIN | 4C | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 23:30,10/Sep | 40 | 06:30,08/Dec | 16
[15 empty] | 4CFLOOR 2MIN | 4C | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,15/Sep | 36 | 04:30,08/Dec | 15
[15 empty] | 4CAUDITORIUMMIN | 4C | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 09:30,27/May | 44 | 02:30,01/Nov | 15
[15 empty] | 4CGYMMIN | 4C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 12:30,05/Feb | 36 | 07:30,07/Feb | 10
[15 empty] | 4CKITCHEN CAFETERIAMIN | 4C | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 15:30,24/Nov | 36 | 07:30,07/Feb | 9
[15 empty] | 4CFLOOR 1MAX | 4C | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,16/Apr | 41 | 13:30,15/Aug | 12
[15 empty] | 4CMECHMAX | 4C | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 11:30,17/Apr | 70 | 17:30,02/Sep | 18
[15 empty] | 4CFLOOR 2MAX | 4C | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,15/Oct | 55 | 14:30,15/Aug | 14
[15 empty] | 4CAUDITORIUMMAX | 4C | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 09:30,30/Nov | 53 | 16:30,11/Jul | 12
[15 empty] | 4CGYMMAX | 4C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 14:30,20/Feb | 59 | 17:30,06/Sep | 12
[15 empty] | 4CKITCHEN CAFETERIAMAX | 4C | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 14:30,27/Feb | 46 | 19:30,15/Aug | 12
[15 empty] | 5ALocationFilename | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 5AFLOOR 15A_TMY7_WA | 5A | People dissatisfied | FLOOR 1 | 5A_TMY7_WA | Percentage (%) | 5 | 07:30,21/Oct | 49 | 11:30,25/Jul | 15
[15 empty] | 5AMECH5A_TMY7_WA | 5A | People dissatisfied | MECH | 5A_TMY7_WA | Percentage (%) | 5 | 08:30,11/May | 69 | 16:30,09/Sep | 21
[15 empty] | 5AFLOOR 25A_TMY7_WA | 5A | People dissatisfied | FLOOR 2 | 5A_TMY7_WA | Percentage (%) | 5 | 07:30,27/Oct | 56 | 13:30,01/Aug | 17
[15 empty] | 5AAUDITORIUM5A_TMY7_WA | 5A | People dissatisfied | AUDITORIUM | 5A_TMY7_WA | Percentage (%) | 5 | 07:30,07/Oct | 63 | 11:30,24/Jul | 16
[15 empty] | 5AGYM5A_TMY7_WA | 5A | People dissatisfied | GYM | 5A_TMY7_WA | Percentage (%) | 5 | 08:30,09/Apr | 39 | 07:30,24/Jan | 11
[15 empty] | 5AKITCHEN CAFETERIA5A_TMY7_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY7_WA | Percentage (%) | 5 | 17:30,31/Dec | 52 | 01:30,19/Jul | 14
[15 empty] | 5AFLOOR 15A_TMY3_WA | 5A | People dissatisfied | FLOOR 1 | 5A_TMY3_WA | Percentage (%) | 5 | 07:30,19/Nov | 51 | 18:30,15/Aug | 15
[15 empty] | 5AMECH5A_TMY3_WA | 5A | People dissatisfied | MECH | 5A_TMY3_WA | Percentage (%) | 5 | 08:30,16/Nov | 69 | 16:30,13/Sep | 21
[15 empty] | 5AFLOOR 25A_TMY3_WA | 5A | People dissatisfied | FLOOR 2 | 5A_TMY3_WA | Percentage (%) | 5 | 07:30,19/Nov | 55 | 16:30,18/Jul | 17
[15 empty] | 5AAUDITORIUM5A_TMY3_WA | 5A | People dissatisfied | AUDITORIUM | 5A_TMY3_WA | Percentage (%) | 5 | 08:30,25/Nov | 61 | 12:30,29/Aug | 16
[15 empty] | 5AGYM5A_TMY3_WA | 5A | People dissatisfied | GYM | 5A_TMY3_WA | Percentage (%) | 5 | 13:30,09/May | 44 | 18:30,23/Sep | 11
[15 empty] | 5AKITCHEN CAFETERIA5A_TMY3_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY3_WA | Percentage (%) | 5 | 16:30,05/Mar | 51 | 23:30,14/Aug | 14
[15 empty] | 5AFLOOR 15A_TMY3 | 5A | People dissatisfied | FLOOR 1 | 5A_TMY3 | Percentage (%) | 5 | 15:30,10/Nov | 53 | 01:30,19/Jul | 15
[15 empty] | 5AMECH5A_TMY3 | 5A | People dissatisfied | MECH | 5A_TMY3 | Percentage (%) | 5 | 01:30,04/May | 69 | 14:30,19/Jul | 21
[15 empty] | 5AFLOOR 25A_TMY3 | 5A | People dissatisfied | FLOOR 2 | 5A_TMY3 | Percentage (%) | 5 | 06:30,20/Apr | 57 | 15:30,18/Jul | 17
[15 empty] | 5AAUDITORIUM5A_TMY3 | 5A | People dissatisfied | AUDITORIUM | 5A_TMY3 | Percentage (%) | 5 | 23:30,05/Oct | 63 | 11:30,17/Jul | 16
[15 empty] | 5AGYM5A_TMY3 | 5A | People dissatisfied | GYM | 5A_TMY3 | Percentage (%) | 5 | 12:30,23/Oct | 47 | 05:30,07/Feb | 11
[15 empty] | 5AKITCHEN CAFETERIA5A_TMY3 | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY3 | Percentage (%) | 5 | 18:30,18/Mar | 59 | 20:30,18/Jul | 14
[15 empty] | 5AFLOOR 15A_TMY2 | 5A | People dissatisfied | FLOOR 1 | 5A_TMY2 | Percentage (%) | 5 | 07:30,01/Oct | 47 | 18:30,18/Jul | 15
[15 empty] | 5AMECH5A_TMY2 | 5A | People dissatisfied | MECH | 5A_TMY2 | Percentage (%) | 5 | 01:30,04/May | 60 | 14:30,19/Jul | 20
[15 empty] | 5AFLOOR 25A_TMY2 | 5A | People dissatisfied | FLOOR 2 | 5A_TMY2 | Percentage (%) | 5 | 07:30,28/Oct | 53 | 19:30,18/Jul | 17
[15 empty] | 5AAUDITORIUM5A_TMY2 | 5A | People dissatisfied | AUDITORIUM | 5A_TMY2 | Percentage (%) | 5 | 18:30,24/Mar | 59 | 13:30,03/Jul | 16
[15 empty] | 5AGYM5A_TMY2 | 5A | People dissatisfied | GYM | 5A_TMY2 | Percentage (%) | 5 | 11:30,08/Mar | 44 | 18:30,26/May | 11
[15 empty] | 5AKITCHEN CAFETERIA5A_TMY2 | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY2 | Percentage (%) | 5 | 17:30,10/Nov | 50 | 19:30,18/Jul | 14
[15 empty] | 5AFLOOR 15A_TMY15_WA | 5A | People dissatisfied | FLOOR 1 | 5A_TMY15_WA | Percentage (%) | 5 | 07:30,19/Nov | 49 | 11:30,25/Jul | 15
[15 empty] | 5AMECH5A_TMY15_WA | 5A | People dissatisfied | MECH | 5A_TMY15_WA | Percentage (%) | 5 | 08:30,16/Nov | 69 | 16:30,13/Sep | 22
[15 empty] | 5AFLOOR 25A_TMY15_WA | 5A | People dissatisfied | FLOOR 2 | 5A_TMY15_WA | Percentage (%) | 5 | 07:30,30/Sep | 56 | 13:30,01/Aug | 17
[15 empty] | 5AAUDITORIUM5A_TMY15_WA | 5A | People dissatisfied | AUDITORIUM | 5A_TMY15_WA | Percentage (%) | 5 | 08:30,25/Nov | 63 | 11:30,24/Jul | 16
[15 empty] | 5AGYM5A_TMY15_WA | 5A | People dissatisfied | GYM | 5A_TMY15_WA | Percentage (%) | 5 | 14:30,03/Apr | 44 | 18:30,23/Sep | 11
[15 empty] | 5AKITCHEN CAFETERIA5A_TMY15_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY15_WA | Percentage (%) | 5 | 12:30,06/Nov | 52 | 01:30,19/Jul | 14
[15 empty] | 5AFLOOR 15A_MIN_WA | 5A | People dissatisfied | FLOOR 1 | 5A_MIN_WA | Percentage (%) | 5 | 07:30,16/Sep | 42 | 04:30,31/Jan | 16
[15 empty] | 5AMECH5A_MIN_WA | 5A | People dissatisfied | MECH | 5A_MIN_WA | Percentage (%) | 5 | 20:30,18/Sep | 43 | 07:30,31/Jan | 19
[15 empty] | 5AFLOOR 25A_MIN_WA | 5A | People dissatisfied | FLOOR 2 | 5A_MIN_WA | Percentage (%) | 5 | 07:30,16/Sep | 41 | 05:30,31/Jan | 16
[15 empty] | 5AAUDITORIUM5A_MIN_WA | 5A | People dissatisfied | AUDITORIUM | 5A_MIN_WA | Percentage (%) | 5 | 21:30,02/Jun | 46 | 03:30,31/Jan | 16
[15 empty] | 5AGYM5A_MIN_WA | 5A | People dissatisfied | GYM | 5A_MIN_WA | Percentage (%) | 5 | 21:30,01/Nov | 47 | 00:30,31/Jan | 11
[15 empty] | 5AKITCHEN CAFETERIA5A_MIN_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_MIN_WA | Percentage (%) | 5 | 18:30,02/Apr | 40 | 01:30,18/Jan | 12
[15 empty] | 5AFLOOR 15A_MAX_WA | 5A | People dissatisfied | FLOOR 1 | 5A_MAX_WA | Percentage (%) | 5 | 07:30,12/Nov | 58 | 02:30,19/Jul | 17
[15 empty] | 5AMECH5A_MAX_WA | 5A | People dissatisfied | MECH | 5A_MAX_WA | Percentage (%) | 5 | 09:30,11/Mar | 79 | 17:30,02/Sep | 26
[15 empty] | 5AFLOOR 25A_MAX_WA | 5A | People dissatisfied | FLOOR 2 | 5A_MAX_WA | Percentage (%) | 5 | 07:30,28/Apr | 58 | 14:30,07/Aug | 19
[15 empty] | 5AAUDITORIUM5A_MAX_WA | 5A | People dissatisfied | AUDITORIUM | 5A_MAX_WA | Percentage (%) | 5 | 12:30,04/Feb | 62 | 13:30,22/Aug | 17
[15 empty] | 5AGYM5A_MAX_WA | 5A | People dissatisfied | GYM | 5A_MAX_WA | Percentage (%) | 5 | 08:30,11/Feb | 48 | 01:30,26/Jul | 12
[15 empty] | 5AKITCHEN CAFETERIA5A_MAX_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_MAX_WA | Percentage (%) | 5 | 17:30,15/Jan | 59 | 03:30,19/Jul | 17
[15 empty] | 5BLocationFilename | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 5BFLOOR 1TMY7WA | 5B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,21/Jun | 41 | 01:30,07/Feb | 14
[15 empty] | 5BMECHTMY7WA | 5B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,19/Jul | 17
[15 empty] | 5BFLOOR 2TMY7WA | 5B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 06:30,11/Aug | 50 | 14:30,18/Jul | 15
[15 empty] | 5BAUDITORIUMTMY7WA | 5B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 16:30,25/Jan | 51 | 15:30,18/Jul | 15
[15 empty] | 5BGYMTMY7WA | 5B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 12:30,04/Mar | 52 | 17:30,03/Sep | 12
[15 empty] | 5BKITCHEN CAFETERIATMY7WA | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 11:30,10/Apr | 39 | 07:30,07/Feb | 11
[15 empty] | 5BFLOOR 1TMY3WA | 5B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 06:30,07/Jun | 38 | 04:30,24/Dec | 13
[15 empty] | 5BMECHTMY3WA | 5B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,19/Jul | 17
[15 empty] | 5BFLOOR 2TMY3WA | 5B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 06:30,11/Aug | 50 | 14:30,18/Jul | 15
[15 empty] | 5BAUDITORIUMTMY3WA | 5B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 18:30,08/Jan | 51 | 15:30,18/Jul | 14
[15 empty] | 5BGYMTMY3WA | 5B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 12:30,13/Jan | 52 | 17:30,03/Sep | 12
[15 empty] | 5BKITCHEN CAFETERIATMY3WA | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 12:30,21/Mar | 35 | 05:30,23/Dec | 11
[15 empty] | 5BFLOOR 1TMY3 | 5B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 22:30,10/Jun | 42 | 04:30,13/Dec | 14
[15 empty] | 5BMECHTMY3 | 5B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 23:30,05/Oct | 69 | 16:30,09/Sep | 19
[15 empty] | 5BFLOOR 2TMY3 | 5B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,14/Sep | 47 | 13:30,01/Aug | 15
[15 empty] | 5BAUDITORIUMTMY3 | 5B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 00:30,11/May | 49 | 16:30,27/Jun | 14
[15 empty] | 5BGYMTMY3 | 5B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 10:30,13/Nov | 63 | 19:30,28/May | 14
[15 empty] | 5BKITCHEN CAFETERIATMY3 | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 17:30,27/Jan | 39 | 21:30,17/Jan | 12
[15 empty] | 5BFLOOR 1TMY2 | 5B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,08/Jun | 42 | 04:30,13/Dec | 14
[15 empty] | 5BMECHTMY2 | 5B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 01:30,10/Jun | 70 | 17:30,02/Sep | 19
[15 empty] | 5BFLOOR 2TMY2 | 5B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,04/Oct | 48 | 14:30,04/Jul | 15
[15 empty] | 5BAUDITORIUMTMY2 | 5B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 22:30,29/May | 50 | 16:30,04/Jul | 15
[15 empty] | 5BGYMTMY2 | 5B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 11:30,01/Mar | 65 | 18:30,02/Sep | 13
[15 empty] | 5BKITCHEN CAFETERIATMY2 | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 15:30,13/Nov | 42 | 19:30,18/Jul | 12
[15 empty] | 5BFLOOR 1TMY15WA | 5B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,03/Jun | 38 | 04:30,24/Dec | 13
[15 empty] | 5BMECHTMY15WA | 5B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,03/Sep | 17
[15 empty] | 5BFLOOR 2TMY15WA | 5B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 06:30,23/Aug | 46 | 14:30,25/Jul | 15
[15 empty] | 5BAUDITORIUMTMY15WA | 5B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 18:30,08/Jan | 49 | 14:30,25/Jul | 14
[15 empty] | 5BGYMTMY15WA | 5B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 11:30,31/Dec | 54 | 18:30,28/May | 12
[15 empty] | 5BKITCHEN CAFETERIATMY15WA | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 12:30,21/Mar | 38 | 04:30,24/Dec | 11
[15 empty] | 5BFLOOR 1MIN | 5B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,12/Jul | 45 | 04:30,06/Dec | 18
[15 empty] | 5BMECHMIN | 5B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 22:30,12/Aug | 51 | 05:30,02/Feb | 21
[15 empty] | 5BFLOOR 2MIN | 5B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,20/Jul | 44 | 04:30,02/Feb | 18
[15 empty] | 5BAUDITORIUMMIN | 5B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 16:30,05/Mar | 48 | 03:30,06/Dec | 18
[15 empty] | 5BGYMMIN | 5B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,17/Nov | 48 | 04:30,06/Dec | 13
[15 empty] | 5BKITCHEN CAFETERIAMIN | 5B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 20:30,14/Jun | 41 | 05:30,06/Dec | 13
[15 empty] | 5BFLOOR 1MAX | 5B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 06:30,05/May | 38 | 15:30,25/Jul | 13
[15 empty] | 5BMECHMAX | 5B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 09:30,20/Apr | 64 | 15:30,03/Sep | 20
[15 empty] | 5BFLOOR 2MAX | 5B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,23/Sep | 48 | 14:30,25/Jul | 15
[15 empty] | 5BAUDITORIUMMAX | 5B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 13:30,07/Dec | 50 | 12:30,25/Jul | 13
[15 empty] | 5BGYMMAX | 5B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 11:30,03/Apr | 63 | 18:30,31/May | 14
[15 empty] | 5BKITCHEN CAFETERIAMAX | 5B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 17:30,02/Feb | 35 | 18:30,25/Jul | 11
[15 empty] | 5CLocationFilename | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 5CFLOOR 1TMY7WA | 5C | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 07:30,07/Oct | 30 | 04:30,04/Jan | 11
[15 empty] | 5CMECHTMY7WA | 5C | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 23:30,24/Jun | 36 | 16:30,15/Sep | 12
[15 empty] | 5CFLOOR 2TMY7WA | 5C | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,04/Oct | 36 | 15:30,18/Jul | 12
[15 empty] | 5CAUDITORIUMTMY7WA | 5C | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 10:30,12/Apr | 40 | 00:30,01/Feb | 11
[15 empty] | 5CGYMTMY7WA | 5C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 07:30,24/May | 36 | 17:30,15/Sep | 9
[15 empty] | 5CKITCHEN CAFETERIATMY7WA | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 17:30,06/Dec | 25 | 10:30,07/Sep | 8
[15 empty] | 5CFLOOR 1TMY3WA | 5C | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,17/May | 28 | 04:30,27/Dec | 10
[15 empty] | 5CMECHTMY3WA | 5C | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 22:30,08/May | 48 | 18:30,28/May | 11
[15 empty] | 5CFLOOR 2TMY3WA | 5C | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,28/Oct | 46 | 15:30,25/Jul | 12
[15 empty] | 5CAUDITORIUMTMY3WA | 5C | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 12:30,15/Jan | 32 | 16:30,25/Jul | 11
[15 empty] | 5CGYMTMY3WA | 5C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 14:30,20/Mar | 61 | 18:30,28/May | 9
[15 empty] | 5CKITCHEN CAFETERIATMY3WA | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 17:30,07/Dec | 30 | 10:30,09/Sep | 9
[15 empty] | 5CFLOOR 1TMY2 | 5C | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 06:30,16/Jun | 45 | 12:30,18/Jul | 15
[15 empty] | 5CMECHTMY2 | 5C | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 10:30,09/Oct | 62 | 17:30,20/Jul | 19
[15 empty] | 5CFLOOR 2TMY2 | 5C | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,30/Apr | 53 | 15:30,18/Jul | 17
[15 empty] | 5CAUDITORIUMTMY2 | 5C | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 14:30,11/Oct | 63 | 14:30,18/Jul | 16
[15 empty] | 5CGYMTMY2 | 5C | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 12:30,26/Sep | 49 | 01:30,08/Mar | 11
[15 empty] | 5CKITCHEN CAFETERIATMY2 | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 17:30,16/Nov | 51 | 04:30,21/Jul | 13
[15 empty] | 5CFLOOR 1TMY15WA | 5C | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,29/Apr | 30 | 15:30,11/Jul | 10
[15 empty] | 5CMECHTMY15WA | 5C | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 23:30,18/Jun | 36 | 15:30,11/Jul | 11
[15 empty] | 5CFLOOR 2TMY15WA | 5C | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,29/Sep | 52 | 14:30,11/Jul | 12
[15 empty] | 5CAUDITORIUMTMY15WA | 5C | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 11:30,01/Apr | 50 | 14:30,11/Jul | 11
[15 empty] | 5CGYMTMY15WA | 5C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 07:30,24/May | 31 | 23:30,31/Oct | 9
[15 empty] | 5CKITCHEN CAFETERIATMY15WA | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 16:30,04/Nov | 32 | 19:30,11/Jul | 8
[15 empty] | 5CFLOOR 1MIN | 5C | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,27/Aug | 39 | 03:30,20/Dec | 14
[15 empty] | 5CMECHMIN | 5C | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 23:30,03/Sep | 46 | 05:30,20/Dec | 16
[15 empty] | 5CFLOOR 2MIN | 5C | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,27/Aug | 38 | 03:30,04/Jan | 14
[15 empty] | 5CAUDITORIUMMIN | 5C | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 12:30,15/Apr | 43 | 16:30,07/Feb | 15
[15 empty] | 5CGYMMIN | 5C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 15:30,15/Jan | 46 | 05:30,20/Dec | 10
[15 empty] | 5CKITCHEN CAFETERIAMIN | 5C | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 19:30,01/Apr | 38 | 02:30,20/Dec | 9
[15 empty] | 5CFLOOR 1MAX | 5C | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,29/Apr | 31 | 15:30,11/Jul | 10
[15 empty] | 5CMECHMAX | 5C | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 15:30,17/Oct | 56 | 19:30,28/May | 13
[15 empty] | 5CFLOOR 2MAX | 5C | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,08/Apr | 53 | 14:30,11/Jul | 13
[15 empty] | 5CAUDITORIUMMAX | 5C | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 21:30,12/Mar | 52 | 18:30,11/Jul | 11
[15 empty] | 5CGYMMAX | 5C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 13:30,24/Oct | 64 | 19:30,28/May | 9
[15 empty] | 5CKITCHEN CAFETERIAMAX | 5C | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 13:30,24/Oct | 38 | 19:30,11/Jul | 10
[15 empty] | 5CFLOOR 1doeCWEC | 5C | People dissatisfied | FLOOR 1 | doeCWEC | Percentage (%) | 5 | 07:30,14/May | 34 | 04:30,22/Nov | 11
[15 empty] | 5CMECHdoeCWEC | 5C | People dissatisfied | MECH | doeCWEC | Percentage (%) | 5 | 01:30,16/Oct | 33 | 04:30,22/Nov | 12
[15 empty] | 5CFLOOR 2doeCWEC | 5C | People dissatisfied | FLOOR 2 | doeCWEC | Percentage (%) | 5 | 07:30,22/Oct | 42 | 16:30,11/Jul | 12
[15 empty] | 5CAUDITORIUMdoeCWEC | 5C | People dissatisfied | AUDITORIUM | doeCWEC | Percentage (%) | 5 | 07:30,08/Jul | 43 | 03:30,22/Nov | 11
[15 empty] | 5CGYMdoeCWEC | 5C | People dissatisfied | GYM | doeCWEC | Percentage (%) | 5 | 15:30,02/May | 34 | 03:30,22/Nov | 9
[15 empty] | 5CKITCHEN CAFETERIAdoeCWEC | 5C | People dissatisfied | KITCHEN CAFETERIA | doeCWEC | Percentage (%) | 5 | 19:30,29/Oct | 26 | 04:30,22/Nov | 9
[15 empty] | 5CFLOOR 1CWEC | 5C | People dissatisfied | FLOOR 1 | CWEC | Percentage (%) | 5 | 07:30,14/May | 33 | 03:30,22/Nov | 11
[15 empty] | 5CMECHCWEC | 5C | People dissatisfied | MECH | CWEC | Percentage (%) | 5 | 01:30,16/Oct | 33 | 04:30,22/Nov | 12
[15 empty] | 5CFLOOR 2CWEC | 5C | People dissatisfied | FLOOR 2 | CWEC | Percentage (%) | 5 | 07:30,22/Oct | 41 | 15:30,11/Jul | 12
[15 empty] | 5CAUDITORIUMCWEC | 5C | People dissatisfied | AUDITORIUM | CWEC | Percentage (%) | 5 | 21:30,10/Mar | 43 | 03:30,22/Nov | 11
[15 empty] | 5CGYMCWEC | 5C | People dissatisfied | GYM | CWEC | Percentage (%) | 5 | 15:30,02/May | 34 | 03:30,22/Nov | 9
[15 empty] | 5CKITCHEN CAFETERIACWEC | 5C | People dissatisfied | KITCHEN CAFETERIA | CWEC | Percentage (%) | 5 | 16:30,24/Dec | 26 | 04:30,22/Nov | 9
[15 empty] | 6ALocationFilename | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 6AFLOOR 1TMY7WA | 6A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,13/May | 45 | 13:30,04/Jul | 15
[15 empty] | 6AMECHTMY7WA | 6A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 22:30,04/Oct | 67 | 17:30,09/Sep | 21
[15 empty] | 6AFLOOR 2TMY7WA | 6A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,13/Oct | 58 | 13:30,08/Aug | 17
[15 empty] | 6AAUDITORIUMTMY7WA | 6A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 01:30,03/Sep | 63 | 17:30,04/Jul | 16
[15 empty] | 6AGYMTMY7WA | 6A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 09:30,22/Mar | 48 | 05:30,24/Jan | 11
[15 empty] | 6AKITCHEN CAFETERIATMY7WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 19:30,03/Nov | 48 | 19:30,04/Jul | 14
[15 empty] | 6AFLOOR 1TMY3WA | 6A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,21/Apr | 52 | 11:30,18/Jul | 15
[15 empty] | 6AMECHTMY3WA | 6A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 15:30,07/Nov | 68 | 18:30,18/Jul | 21
[15 empty] | 6AFLOOR 2TMY3WA | 6A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,16/Apr | 59 | 11:30,18/Jul | 17
[15 empty] | 6AAUDITORIUMTMY3WA | 6A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 19:30,23/Feb | 65 | 12:30,17/Jul | 16
[15 empty] | 6AGYMTMY3WA | 6A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 13:30,13/Mar | 49 | 17:30,21/May | 11
[15 empty] | 6AKITCHEN CAFETERIATMY3WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 15:30,24/Oct | 59 | 19:30,18/Jul | 14
[15 empty] | 6AFLOOR 1TMY3 | 6A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 06:30,07/May | 50 | 12:30,04/Jul | 16
[15 empty] | 6AMECHTMY3 | 6A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 01:30,05/May | 65 | 17:30,19/Jul | 21
[15 empty] | 6AFLOOR 2TMY3 | 6A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,19/Apr | 56 | 15:30,18/Jul | 18
[15 empty] | 6AAUDITORIUMTMY3 | 6A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 20:30,01/Dec | 64 | 14:30,01/Aug | 17
[15 empty] | 6AGYMTMY3 | 6A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,20/Dec | 50 | 04:30,31/Jan | 12
[15 empty] | 6AKITCHEN CAFETERIATMY3 | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 17:30,01/Mar | 57 | 20:30,18/Jul | 14
[15 empty] | 6AFLOOR 1TMY2 | 6A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,10/May | 47 | 12:30,18/Jul | 16
[15 empty] | 6AMECHTMY2 | 6A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 15:30,03/Oct | 64 | 18:30,28/May | 21
[15 empty] | 6AFLOOR 2TMY2 | 6A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,26/Mar | 52 | 17:30,18/Jul | 18
[15 empty] | 6AAUDITORIUMTMY2 | 6A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 16:30,16/Mar | 61 | 16:30,17/Jul | 16
[15 empty] | 6AGYMTMY2 | 6A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 15:30,25/Sep | 48 | 07:30,10/Jan | 12
[15 empty] | 6AKITCHEN CAFETERIATMY2 | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 17:30,19/Nov | 49 | 07:30,18/Jul | 14
[15 empty] | 6AFLOOR 1TMY15WA | 6A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,13/May | 50 | 17:30,04/Jul | 15
[15 empty] | 6AMECHTMY15WA | 6A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 04:30,06/Oct | 66 | 18:30,04/Jul | 22
[15 empty] | 6AFLOOR 2TMY15WA | 6A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,13/Oct | 58 | 15:30,03/Jul | 17
[15 empty] | 6AAUDITORIUMTMY15WA | 6A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 21:30,08/Apr | 61 | 11:30,08/Aug | 16
[15 empty] | 6AGYMTMY15WA | 6A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,24/Mar | 42 | 19:30,04/Jul | 12
[15 empty] | 6AKITCHEN CAFETERIATMY15WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 13:30,02/Oct | 57 | 19:30,04/Jul | 14
[15 empty] | 6AFLOOR 1MIN | 6A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,25/Jun | 44 | 04:30,01/Feb | 17
[15 empty] | 6AMECHMIN | 6A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 08:30,28/Jun | 45 | 06:30,21/Jan | 21
[15 empty] | 6AFLOOR 2MIN | 6A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,25/Jun | 44 | 04:30,21/Jan | 18
[15 empty] | 6AAUDITORIUMMIN | 6A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 12:30,17/May | 51 | 05:30,01/Feb | 17
[15 empty] | 6AGYMMIN | 6A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,15/Mar | 49 | 06:30,03/Jan | 12
[15 empty] | 6AKITCHEN CAFETERIAMIN | 6A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 15:30,26/Sep | 40 | 04:30,31/Jan | 13
[15 empty] | 6AFLOOR 1MAX | 6A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,08/Apr | 58 | 19:30,18/Jul | 18
[15 empty] | 6AMECHMAX | 6A | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 09:30,26/Nov | 85 | 19:30,18/Jul | 29
[15 empty] | 6AFLOOR 2MAX | 6A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,15/Oct | 60 | 17:30,18/Jul | 20
[15 empty] | 6AAUDITORIUMMAX | 6A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 14:30,08/Jan | 65 | 13:30,18/Jul | 18
[15 empty] | 6AGYMMAX | 6A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,03/Mar | 63 | 05:30,19/Jul | 14
[15 empty] | 6AKITCHEN CAFETERIAMAX | 6A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 13:30,20/Nov | 60 | 18:30,18/Jul | 17
[15 empty] | 6BLocationFilename | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 6BFLOOR 1TMY7WA | 6B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 10 | 07:30,23/Jul | 63 | 04:30,10/May | 36
[15 empty] | 6BMECHTMY7WA | 6B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 32 | 07:30,19/Jan | 93 | 19:30,07/Apr | 65
[15 empty] | 6BFLOOR 2TMY7WA | 6B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 8 | 07:30,19/Jan | 60 | 03:30,05/Apr | 37
[15 empty] | 6BAUDITORIUMTMY7WA | 6B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 11 | 21:30,24/Dec | 78 | 18:30,24/May | 37
[15 empty] | 6BGYMTMY7WA | 6B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 9 | 08:30,19/Jan | 54 | 05:30,06/Apr | 22
[15 empty] | 6BKITCHEN CAFETERIATMY7WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 15 | 07:30,28/Jul | 84 | 13:30,03/Sep | 38
[15 empty] | 6BFLOOR 1TMY3WA | 6B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,02/Jun | 38 | 17:30,18/Jul | 14
[15 empty] | 6BMECHTMY3WA | 6B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 23:30,07/Oct | 63 | 16:30,22/Jul | 18
[15 empty] | 6BFLOOR 2TMY3WA | 6B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,27/May | 53 | 15:30,25/Jul | 15
[15 empty] | 6BAUDITORIUMTMY3WA | 6B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 03:30,11/Jul | 52 | 16:30,18/Jul | 15
[15 empty] | 6BGYMTMY3WA | 6B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 13:30,15/Mar | 59 | 18:30,01/Sep | 13
[15 empty] | 6BKITCHEN CAFETERIATMY3WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 16:30,22/Mar | 39 | 19:30,18/Jul | 11
[15 empty] | 6BFLOOR 1TMY3 | 6B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,20/May | 40 | 01:30,27/Dec | 13
[15 empty] | 6BMECHTMY3 | 6B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 09:30,15/May | 55 | 17:30,15/Sep | 18
[15 empty] | 6BFLOOR 2TMY3 | 6B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,22/Jun | 50 | 15:30,08/Aug | 15
[15 empty] | 6BAUDITORIUMTMY3 | 6B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 20:30,03/Dec | 47 | 16:30,08/Aug | 14
[15 empty] | 6BGYMTMY3 | 6B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 14:30,22/Jan | 58 | 18:30,25/May | 12
[15 empty] | 6BKITCHEN CAFETERIATMY3 | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 16:30,08/Mar | 39 | 01:30,18/Jan | 11
[15 empty] | 6BFLOOR 1TMY2 | 6B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,11/Jun | 43 | 05:30,12/Dec | 14
[15 empty] | 6BMECHTMY2 | 6B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 01:30,18/Jun | 57 | 15:30,30/Jun | 18
[15 empty] | 6BFLOOR 2TMY2 | 6B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,01/Sep | 48 | 15:30,26/Jun | 15
[15 empty] | 6BAUDITORIUMTMY2 | 6B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 11:30,20/Apr | 50 | 06:30,12/Dec | 15
[15 empty] | 6BGYMTMY2 | 6B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,05/Oct | 54 | 17:30,02/Sep | 12
[15 empty] | 6BKITCHEN CAFETERIATMY2 | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 18:30,30/Dec | 40 | 05:30,13/Dec | 11
[15 empty] | 6BFLOOR 1TMY15WA | 6B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,17/Jun | 35 | 04:30,30/Dec | 13
[15 empty] | 6BMECHTMY15WA | 6B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 08:30,23/Jun | 57 | 14:30,29/Jul | 17
[15 empty] | 6BFLOOR 2TMY15WA | 6B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,24/Sep | 46 | 14:30,25/Jul | 15
[15 empty] | 6BAUDITORIUMTMY15WA | 6B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 18:30,12/Jan | 50 | 14:30,24/Jul | 14
[15 empty] | 6BGYMTMY15WA | 6B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,24/May | 58 | 18:30,02/Sep | 12
[15 empty] | 6BKITCHEN CAFETERIATMY15WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 12:30,16/Oct | 37 | 05:30,30/Dec | 10
[15 empty] | 6BFLOOR 1MIN | 6B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,11/Aug | 43 | 04:30,06/Dec | 18
[15 empty] | 6BMECHMIN | 6B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 22:30,11/Aug | 48 | 06:30,17/Feb | 23
[15 empty] | 6BFLOOR 2MIN | 6B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,11/Aug | 45 | 04:30,17/Feb | 19
[15 empty] | 6BAUDITORIUMMIN | 6B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 17:30,04/Mar | 50 | 04:30,20/Dec | 19
[15 empty] | 6BGYMMIN | 6B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 17:30,08/Jun | 49 | 02:30,05/Dec | 13
[15 empty] | 6BKITCHEN CAFETERIAMIN | 6B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 10:30,04/Sep | 42 | 05:30,18/Feb | 14
[15 empty] | 6BFLOOR 1MAX | 6B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 06:30,12/May | 40 | 13:30,01/Aug | 13
[15 empty] | 6BMECHMAX | 6B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 22:30,28/Oct | 68 | 14:30,16/Jul | 20
[15 empty] | 6BFLOOR 2MAX | 6B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,21/Sep | 50 | 12:30,01/Aug | 15
[15 empty] | 6BAUDITORIUMMAX | 6B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 19:30,09/Feb | 49 | 13:30,18/Jul | 14
[15 empty] | 6BGYMMAX | 6B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 13:30,13/Mar | 65 | 18:30,03/Sep | 15
[15 empty] | 6BKITCHEN CAFETERIAMAX | 6B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 11:30,06/Nov | 41 | 19:30,01/Aug | 11
[15 empty] | 7LocationFilename | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 7FLOOR 1TMY7WA | 7 | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 07:30,22/Sep | 42 | 13:30,04/Jul | 15
[15 empty] | 7MECHTMY7WA | 7 | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 23:30,06/Oct | 55 | 14:30,07/Sep | 19
[15 empty] | 7FLOOR 2TMY7WA | 7 | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,21/Sep | 51 | 15:30,04/Jul | 16
[15 empty] | 7AUDITORIUMTMY7WA | 7 | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 10:30,20/Oct | 59 | 16:30,04/Jul | 15
[15 empty] | 7GYMTMY7WA | 7 | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 11:30,19/Jan | 46 | 07:30,03/Jan | 11
[15 empty] | 7KITCHEN CAFETERIATMY7WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 18:30,02/Nov | 46 | 07:30,04/Jul | 13
[15 empty] | 7FLOOR 1TMY3WA | 7 | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 06:30,25/May | 47 | 16:30,04/Jul | 14
[15 empty] | 7MECHTMY3WA | 7 | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 22:30,13/May | 58 | 15:30,31/May | 18
[15 empty] | 7FLOOR 2TMY3WA | 7 | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,24/Mar | 57 | 16:30,04/Jul | 16
[15 empty] | 7AUDITORIUMTMY3WA | 7 | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 13:30,07/Apr | 60 | 11:30,04/Jul | 15
[15 empty] | 7GYMTMY3WA | 7 | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 11:30,25/Jan | 49 | 17:30,05/May | 11
[15 empty] | 7KITCHEN CAFETERIATMY3WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 17:30,22/Nov | 48 | 07:30,04/Jul | 12
[15 empty] | 7FLOOR 1TMY3 | 7 | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,12/May | 42 | 03:30,20/Dec | 15
[15 empty] | 7MECHTMY3 | 7 | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 23:30,29/Sep | 44 | 16:30,26/May | 19
[15 empty] | 7FLOOR 2TMY3 | 7 | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,10/Sep | 54 | 14:30,17/Jul | 16
[15 empty] | 7AUDITORIUMTMY3 | 7 | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 20:30,22/Mar | 57 | 16:30,18/Jul | 16
[15 empty] | 7GYMTMY3 | 7 | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,26/Feb | 49 | 00:30,20/Dec | 11
[15 empty] | 7KITCHEN CAFETERIATMY3 | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 18:30,13/Apr | 45 | 18:30,18/Jul | 12
[15 empty] | 7FLOOR 1TMY2 | 7 | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,24/Jun | 43 | 04:30,01/Feb | 15
[15 empty] | 7MECHTMY2 | 7 | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 21:30,05/Jun | 47 | 16:30,08/Jul | 19
[15 empty] | 7FLOOR 2TMY2 | 7 | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,23/Jun | 50 | 16:30,11/Jul | 16
[15 empty] | 7AUDITORIUMTMY2 | 7 | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 09:30,12/May | 51 | 05:30,08/Feb | 16
[15 empty] | 7GYMTMY2 | 7 | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 14:30,12/Feb | 49 | 01:30,01/Feb | 11
[15 empty] | 7KITCHEN CAFETERIATMY2 | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 19:30,02/Nov | 43 | 20:30,11/Jul | 12
[15 empty] | 7FLOOR 1TMY15WA | 7 | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,15/Oct | 51 | 10:30,18/Jul | 14
[15 empty] | 7MECHTMY15WA | 7 | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 23:30,15/Apr | 60 | 12:30,18/Jul | 18
[15 empty] | 7FLOOR 2TMY15WA | 7 | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,30/Sep | 57 | 12:30,18/Jul | 16
[15 empty] | 7AUDITORIUMTMY15WA | 7 | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 20:30,19/Feb | 65 | 12:30,17/Jul | 15
[15 empty] | 7GYMTMY15WA | 7 | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 11:30,01/Mar | 37 | 05:30,25/Jan | 11
[15 empty] | 7KITCHEN CAFETERIATMY15WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 12:30,13/Nov | 53 | 07:30,18/Jul | 13
[15 empty] | 7FLOOR 1MIN | 7 | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,20/Aug | 45 | 18:30,17/Jan | 17
[15 empty] | 7MECHMIN | 7 | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 09:30,12/Aug | 47 | 19:30,17/Jan | 21
[15 empty] | 7FLOOR 2MIN | 7 | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,27/Jul | 46 | 07:30,17/Jan | 18
[15 empty] | 7AUDITORIUMMIN | 7 | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 19:30,26/Mar | 51 | 22:30,17/Jan | 18
[15 empty] | 7GYMMIN | 7 | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 16:30,23/Mar | 49 | 07:30,17/Jan | 12
[15 empty] | 7KITCHEN CAFETERIAMIN | 7 | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 16:30,07/Oct | 43 | 22:30,17/Jan | 13
[15 empty] | 7FLOOR 1MAX | 7 | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,26/Apr | 56 | 09:30,18/Jul | 16
[15 empty] | 7MECHMAX | 7 | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 23:30,11/Apr | 73 | 13:30,18/Jul | 24
[15 empty] | 7FLOOR 2MAX | 7 | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,15/Oct | 59 | 13:30,18/Jul | 18
[15 empty] | 7AUDITORIUMMAX | 7 | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 13:30,05/Apr | 64 | 10:30,18/Jul | 16
[15 empty] | 7GYMMAX | 7 | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,13/Mar | 50 | 17:30,29/Sep | 12
[15 empty] | 7KITCHEN CAFETERIAMAX | 7 | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 15:30,03/Apr | 56 | 19:30,18/Jul | 15
[15 empty] | 8LocationFilename | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 8FLOOR 1TMY7WA | 8 | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,20/Aug | 44 | 03:30,28/Jan | 16
[15 empty] | 8MECHTMY7WA | 8 | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 00:30,04/Sep | 45 | 04:30,28/Jan | 20
[15 empty] | 8FLOOR 2TMY7WA | 8 | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,26/Jan | 17
[15 empty] | 8AUDITORIUMTMY7WA | 8 | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 23:30,19/May | 48 | 05:30,19/Dec | 16
[15 empty] | 8GYMTMY7WA | 8 | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 10:30,13/Jun | 55 | 19:30,26/May | 12
[15 empty] | 8KITCHEN CAFETERIATMY7WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 17:30,02/Apr | 43 | 20:30,27/Jan | 13
[15 empty] | 8FLOOR 1TMY3WA | 8 | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 06:30,02/Sep | 42 | 00:30,06/Dec | 15
[15 empty] | 8MECHTMY3WA | 8 | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 00:30,11/Sep | 54 | 16:30,28/Jun | 20
[15 empty] | 8FLOOR 2TMY3WA | 8 | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,27/Aug | 51 | 15:30,19/Jun | 17
[15 empty] | 8AUDITORIUMTMY3WA | 8 | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 10:30,28/Apr | 50 | 15:30,19/Jun | 16
[15 empty] | 8GYMTMY3WA | 8 | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 14:30,05/Mar | 52 | 18:30,12/May | 12
[15 empty] | 8KITCHEN CAFETERIATMY3WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 17:30,08/Apr | 41 | 21:30,27/Jun | 12
[15 empty] | 8FLOOR 1TMY3 | 8 | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,19/May | 44 | 04:30,01/Mar | 16
[15 empty] | 8MECHTMY3 | 8 | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 22:30,19/Aug | 45 | 04:30,01/Mar | 21
[15 empty] | 8FLOOR 2TMY3 | 8 | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,12/Jan | 18
[15 empty] | 8AUDITORIUMTMY3 | 8 | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 16:30,11/Mar | 52 | 04:30,01/Mar | 17
[15 empty] | 8GYMTMY3 | 8 | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 10:30,21/Aug | 50 | 20:30,05/Dec | 12
[15 empty] | 8KITCHEN CAFETERIATMY3 | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 17:30,29/Sep | 41 | 02:30,01/Mar | 14
[15 empty] | 8FLOOR 1TMY2 | 8 | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,03/Jun | 49 | 04:30,04/Jan | 17
[15 empty] | 8MECHTMY2 | 8 | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 09:30,13/Jun | 50 | 05:30,04/Jan | 21
[15 empty] | 8FLOOR 2TMY2 | 8 | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,27/Aug | 49 | 01:30,04/Jan | 18
[15 empty] | 8AUDITORIUMTMY2 | 8 | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 13:30,18/May | 55 | 01:30,04/Jan | 18
[15 empty] | 8GYMTMY2 | 8 | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 15:30,19/Mar | 52 | 04:30,03/Jan | 12
[15 empty] | 8KITCHEN CAFETERIATMY2 | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 20:30,22/Apr | 47 | 05:30,04/Jan | 14
[15 empty] | 8FLOOR 1TMY15WA | 8 | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,21/May | 40 | 06:30,21/Feb | 16
[15 empty] | 8MECHTMY15WA | 8 | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 09:30,23/Sep | 54 | 16:30,28/Jun | 20
[15 empty] | 8FLOOR 2TMY15WA | 8 | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,22/Sep | 51 | 15:30,19/Jun | 17
[15 empty] | 8AUDITORIUMTMY15WA | 8 | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 18:30,12/Feb | 50 | 15:30,19/Jun | 16
[15 empty] | 8GYMTMY15WA | 8 | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 10:30,28/Oct | 47 | 04:30,21/Feb | 12
[15 empty] | 8KITCHEN CAFETERIATMY15WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 17:30,07/Apr | 41 | 21:30,27/Jun | 13
[15 empty] | 8FLOOR 1MIN | 8 | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,02/Jul | 49 | 03:30,18/Jan | 21
[15 empty] | 8MECHMIN | 8 | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 11:30,15/Jul | 51 | 06:30,11/Jan | 26
[15 empty] | 8FLOOR 2MIN | 8 | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,16/Jul | 50 | 04:30,11/Jan | 21
[15 empty] | 8AUDITORIUMMIN | 8 | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 13:30,03/Sep | 56 | 05:30,11/Jan | 22
[15 empty] | 8GYMMIN | 8 | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 12:30,12/Oct | 52 | 04:30,01/Feb | 14
[15 empty] | 8KITCHEN CAFETERIAMIN | 8 | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 17:30,31/Aug | 47 | 05:30,11/Jan | 16
[15 empty] | 8FLOOR 1MAX | 8 | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,24/Sep | 40 | 20:30,27/Jun | 15
[15 empty] | 8MECHMAX | 8 | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 01:30,02/Oct | 68 | 18:30,28/May | 20
[15 empty] | 8FLOOR 2MAX | 8 | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,31/Aug | 51 | 15:30,20/Jun | 17
[15 empty] | 8AUDITORIUMMAX | 8 | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 10:30,08/Oct | 50 | 16:30,03/Jul | 15
[15 empty] | 8GYMMAX | 8 | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,12/Sep | 66 | 18:30,25/May | 14
[15 empty] | 8KITCHEN CAFETERIAMAX | 8 | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 14:30,09/Oct | 45 | 22:30,27/Jun | 12

## 2s Summary of Results
| Building Area (ft2): | 211975
1A - Miami | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 4560433 | 3531758 | 2701816 | 175825 | 2023218 | 5577495 | 0 | 225431 | 345722 | 34299 | 1228691 | 19175997 | 90.4635 | max EUI | max EUI
| TMY3 DOE | 4558776 | 3680972 | 2701816 | 178641 | 2023218 | 5579778 | 0 | 234956 | 345722 | 34299 | 1228691 | 19338178 | 91.2286 | 94.3934 | 91.2286
| TMY3 WA | 3630714 | 4394126 | 2701816 | 180906 | 2023218 | 5691870 | 0 | 280476 | 345722 | 34299 | 1228691 | 19283147 | 90.969 | min EUI | min EUI
| TMY7 WA | 4037962 | 3928257 | 2701816 | 182207 | 2023218 | 5626283 | 0 | 250740 | 345722 | 34299 | 1228691 | 19130504 | 90.2489 | 88.9777 | 88.9777
| TMY15 WA | 3615719 | 4046356 | 2701816 | 181525 | 2023218 | 5654122 | 0 | 258278 | 345722 | 34299 | 1228691 | 18861055 | 88.9777 | variance | variance
| XMY Min WA | 6785897 | 2618802 | 2701816 | 183602 | 2023218 | 5148525 | 0 | 167158 | 345722 | 34299 | 1228691 | 20009039 | 94.3934 | 5.936% | 2.467%
| XMY Max WA | 3163862 | 4770494 | 2701816 | 178359 | 2023218 | 5734493 | 0 | 304500 | 345722 | 34299 | 1228691 | 19256763 | 90.8445
2A - Houston | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5447643 | 2855987 | 2701816 | 177640 | 2023218 | 5234597 | 0 | 182297 | 345722 | 34299 | 1228691 | 19003219 | 89.6484 | max EUI | max EUI
| TMY3 DOE | 5333076 | 2906149 | 2701816 | 179554 | 2023218 | 5261729 | 0 | 185499 | 345722 | 34299 | 1228691 | 18971062 | 89.4967 | 99.4892 | 89.6484
| TMY3 WA | 3553338 | 3463519 | 2701816 | 186049 | 2023218 | 5318483 | 0 | 221076 | 345722 | 34299 | 1228691 | 17847520 | 84.1963 | min EUI | min EUI
| TMY7 WA | 4215784 | 3187865 | 2701816 | 186368 | 2023218 | 5307219 | 0 | 203481 | 345722 | 34299 | 1228691 | 18205772 | 85.8864 | 82.2074 | 84.1963
| TMY15 WA | 4191936 | 3330850 | 2701816 | 185961 | 2023218 | 5329321 | 0 | 212607 | 345722 | 34299 | 1228691 | 18355730 | 86.5938 | variance | variance
| XMY Min WA | 8935379 | 1929405 | 2701816 | 195846 | 2023218 | 4800385 | 0 | 123154 | 345722 | 34299 | 1228691 | 21089224 | 99.4892 | 19.31% | 6.092%
| XMY Max WA | 2316295 | 4159931 | 2701816 | 183590 | 2023218 | 5395507 | 0 | 265528 | 345722 | 34299 | 1228691 | 17425906 | 82.2074
2B - Phoenix | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 3518726 | 2742273 | 2701816 | 175394 | 2023218 | 6095808 | 0 | 175039 | 345722 | 34299 | 1228691 | 17812295 | 84.0302 | max EUI | max EUI
| TMY3 DOE | 3160343 | 2972282 | 2701816 | 177114 | 2023218 | 6137437 | 0 | 189720 | 345722 | 34299 | 1228691 | 17741951 | 83.6983 | 90.754 | 84.0302
| TMY3 WA | 2697613 | 2965328 | 2701816 | 181625 | 2023218 | 6104335 | 0 | 189276 | 345722 | 34299 | 1228691 | 17243232 | 81.3456 | min EUI | min EUI
| TMY7 WA | 2948141 | 2615443 | 2701816 | 180843 | 2023218 | 6088575 | 0 | 166943 | 345722 | 34299 | 1228691 | 17105000 | 80.6935 | 80.3148 | 80.6935
| TMY15 WA | 2908243 | 2796246 | 2701816 | 181125 | 2023218 | 6103424 | 0 | 178484 | 345722 | 34299 | 1228691 | 17272577 | 81.484 | variance | variance
| XMY Min WA | 6395818 | 1546407 | 2701816 | 181419 | 2023218 | 5910170 | 0 | 98707 | 345722 | 34299 | 1228691 | 19237576 | 90.754 | 12.47% | 3.987%
| XMY Max WA | 1756523 | 3604918 | 2701816 | 179385 | 2023218 | 6148754 | 0 | 230101 | 345722 | 34299 | 1228691 | 17024736 | 80.3148
3A - Atlanta | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 7100293 | 1741083 | 2701816 | 177771 | 2023218 | 4619997 | 0 | 111133 | 345722 | 34299 | 1228691 | 18855332 | 88.9507 | max EUI | max EUI
| TMY3 DOE | 6717984 | 1872167 | 2701816 | 180756 | 2023218 | 4656455 | 0 | 119500 | 345722 | 34299 | 1228691 | 18651917 | 87.9911 | 98.9415 | 88.9507
| TMY3 WA | 5421714 | 2277426 | 2701816 | 188858 | 2023218 | 4763153 | 0 | 145368 | 345722 | 34299 | 1228691 | 17901574 | 84.4513 | min EUI | min EUI
| TMY7 WA | 6037285 | 2060006 | 2701816 | 189208 | 2023218 | 4666561 | 0 | 131490 | 345722 | 34299 | 1228691 | 18189605 | 85.8101 | 80.114 | 84.0531
| TMY15 WA | 5528712 | 2131943 | 2701816 | 188094 | 2023218 | 4727274 | 0 | 136081 | 345722 | 34299 | 1228691 | 17817159 | 84.0531 | variance | variance
| XMY Min WA | 10504105 | 1004908 | 2701816 | 187506 | 2023218 | 4107412 | 0 | 64143 | 345722 | 34299 | 1228691 | 20973129 | 98.9415 | 21.4% | 5.566%
| XMY Max WA | 3626396 | 2862468 | 2701816 | 189433 | 2023218 | 5016095 | 0 | 182711 | 345722 | 34299 | 1228691 | 16982158 | 80.114
3B - Las Vegas | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 4888554 | 1875900 | 2701816 | 174724 | 2023218 | 5516096 | 0 | 119738 | 345722 | 34299 | 1228691 | 17680067 | 83.4064 | max EUI | max EUI
| TMY3 DOE | 4869774 | 1964613 | 2701816 | 177559 | 2023218 | 5511964 | 0 | 125401 | 345722 | 34299 | 1228691 | 17754366 | 83.7569 | 93.92 | 83.7569
| TMY3 WA | 4255632 | 2084287 | 2701816 | 180956 | 2023218 | 5519496 | 0 | 133040 | 345722 | 34299 | 1228691 | 17278466 | 81.5118 | min EUI | min EUI
| TMY7 WA | 4472989 | 1866050 | 2701816 | 180831 | 2023218 | 5491405 | 0 | 119110 | 345722 | 34299 | 1228691 | 17235440 | 81.3088 | 78.9735 | 81.3088
| TMY15 WA | 4533011 | 1910527 | 2701816 | 180906 | 2023218 | 5489366 | 0 | 121949 | 345722 | 34299 | 1228691 | 17340814 | 81.8059 | variance | variance
| XMY Min WA | 8510766 | 905949 | 2701816 | 180599 | 2023218 | 5148503 | 0 | 57827 | 345722 | 34299 | 1228691 | 19908699 | 93.92 | 17.85% | 2.923%
| XMY Max WA | 2964091 | 2685922 | 2701816 | 179980 | 2023218 | 5633920 | 0 | 171442 | 345722 | 34299 | 1228691 | 16740410 | 78.9735
3C - San Francisco | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 8440071 | 697331 | 2701816 | 179911 | 2023218 | 4461924 | 0 | 44510 | 345722 | 34299 | 1228691 | 18928802 | 89.2973 | max EUI | max EUI
| TMY3 DOE | 8011237 | 776409 | 2701816 | 181650 | 2023218 | 4540145 | 0 | 49558 | 345722 | 34299 | 1228691 | 18664054 | 88.0484 | 96.0554 | 89.9976
| TMY3 WA | 6872394 | 853659 | 2701816 | 185980 | 2023218 | 4607605 | 0 | 54489 | 345722 | 34299 | 1228691 | 17679182 | 83.4022 | min EUI | min EUI
| TMY7 WA | 8462511 | 765132 | 2701816 | 188245 | 2023218 | 4507462 | 0 | 48838 | 345722 | 34299 | 1228691 | 19077243 | 89.9976 | 78.2342 | 83.4022
| TMY15 WA | 7676660 | 716347 | 2701816 | 187331 | 2023218 | 4539482 | 0 | 45724 | 345722 | 34299 | 1228691 | 18270599 | 86.1922 | variance | variance
| XMY Min WA | 10309754 | 488754 | 2701816 | 183577 | 2023218 | 4243011 | 0 | 31197 | 345722 | 34299 | 1228691 | 20361348 | 96.0554 | 20.24% | 7.491%
| XMY Max WA | 5579321 | 992857 | 2701816 | 183202 | 2023218 | 4659896 | 0 | 63374 | 345722 | 34299 | 1228691 | 16583705 | 78.2342
4A - Baltimore | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 7587562 | 2244353 | 2701816 | 182245 | 2023218 | 2083298 | 22098 | 143257 | 345722 | 34299 | 1228691 | 17367868 | 81.9336 | max EUI | max EUI
| TMY3 DOE | 6984433 | 2285566 | 2701816 | 182689 | 2023218 | 2048636 | 20486 | 145887 | 345722 | 34299 | 1228691 | 16772752 | 79.1261 | 106.1223 | 81.9336
| TMY3 WA | 4938949 | 2726518 | 2701816 | 190372 | 2023218 | 1988569 | 15072 | 174033 | 345722 | 34299 | 1228691 | 15138568 | 71.4168 | min EUI | min EUI
| TMY7 WA | 5829871 | 2537798 | 2701816 | 191116 | 2023218 | 2018025 | 17422 | 161987 | 345722 | 34299 | 1228691 | 15861274 | 74.8262 | 64.1794 | 71.4168
| TMY15 WA | 5227628 | 2690388 | 2701816 | 189302 | 2023218 | 2013093 | 15797 | 171727 | 345722 | 34299 | 1228691 | 15412990 | 72.7114 | variance | variance
| XMY Min WA | 13162845 | 1577092 | 2701816 | 193519 | 2023218 | 2320154 | 35939 | 100665 | 345722 | 34299 | 1228691 | 22495269 | 106.1223 | 53.01% | 13.29%
| XMY Max WA | 2633453 | 3577343 | 2701816 | 191273 | 2023218 | 1860798 | 8173 | 228341 | 345722 | 34299 | 1228691 | 13604436 | 64.1794
4B - Albuquerque | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 6126015 | 1734473 | 2701816 | 177490 | 2023218 | 2104640 | 19037 | 110711 | 345722 | 34299 | 1228691 | 15377421 | 72.5436 | max EUI | max EUI
| TMY3 DOE | 5627729 | 1712471 | 2701816 | 178747 | 2023218 | 2078261 | 17735 | 109307 | 345722 | 34299 | 1228691 | 14829305 | 69.9578 | 100.7986 | 73.1734
| TMY3 WA | 4884193 | 2012595 | 2701816 | 180756 | 2023218 | 2113181 | 16058 | 128463 | 345722 | 34299 | 1228691 | 14440301 | 68.1227 | min EUI | min EUI
| TMY7 WA | 5954332 | 1951337 | 2701816 | 181037 | 2023218 | 2175760 | 18849 | 124553 | 345722 | 34299 | 1228691 | 15510923 | 73.1734 | 62.7761 | 68.1227
| TMY15 WA | 5751131 | 1993426 | 2701816 | 181043 | 2023218 | 2155856 | 18330 | 127240 | 345722 | 34299 | 1228691 | 15332081 | 72.3297 | variance | variance
| XMY Min WA | 12135627 | 1415660 | 2701816 | 181150 | 2023218 | 2404844 | 34083 | 90361 | 345722 | 34299 | 1228691 | 21366780 | 100.7986 | 54.35% | 7.22%
| XMY Max WA | 3452860 | 2377847 | 2701816 | 179748 | 2023218 | 2027691 | 11995 | 151778 | 345722 | 34299 | 1228691 | 13306974 | 62.7761
4C - Portland | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 6760974 | 1378925 | 2701816 | 184760 | 2023218 | 1967100 | 19828 | 88017 | 345722 | 34299 | 1228691 | 15504659 | 73.1438 | max EUI | max EUI
| TMY3 DOE | 6402976 | 1416257 | 2701816 | 186856 | 2023218 | 1949359 | 18876 | 90399 | 345722 | 34299 | 1228691 | 15169778 | 71.564 | 106.4694 | 76.0041
| TMY3 WA | 5898545 | 1587219 | 2701816 | 199050 | 2023218 | 1957595 | 17870 | 101312 | 345722 | 34299 | 1228691 | 14866646 | 70.134 | min EUI | min EUI
| TMY7 WA | 6971064 | 1639215 | 2701816 | 195840 | 2023218 | 2074651 | 20519 | 104631 | 345722 | 34299 | 1228691 | 16110975 | 76.0041 | 62.1802 | 70.134
| TMY15 WA | 6390305 | 1626053 | 2701816 | 196879 | 2023218 | 2013593 | 19213 | 103791 | 345722 | 34299 | 1228691 | 15454889 | 72.909 | variance | variance
| XMY Min WA | 13429492 | 1249539 | 2701816 | 194088 | 2023218 | 2474665 | 36252 | 79758 | 345722 | 34299 | 1228691 | 22568849 | 106.4694 | 61.89% | 8.203%
| XMY Max WA | 3801351 | 2081471 | 2701816 | 199563 | 2023218 | 1847960 | 12394 | 132860 | 345722 | 34299 | 1228691 | 13180654 | 62.1802
5A - Chicago | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 10599150 | 1959621 | 2701816 | 181694 | 2023218 | 2232446 | 31365 | 125082 | 345722 | 34299 | 1228691 | 20234413 | 95.4566 | max EUI | max EUI
| TMY3 DOE | 10374174 | 2025544 | 2701816 | 183540 | 2023218 | 2216441 | 30773 | 129290 | 345722 | 34299 | 1228691 | 20064817 | 94.6565 | 130.3891 | 95.4566
| TMY3 WA | 7158250 | 2199430 | 2701816 | 191961 | 2023218 | 2059362 | 22486 | 140389 | 345722 | 34299 | 1228691 | 16876933 | 79.6176 | min EUI | min EUI
| TMY7 WA | 8923955 | 2095367 | 2701816 | 190991 | 2023218 | 2166836 | 27269 | 133747 | 345722 | 34299 | 1228691 | 18643220 | 87.9501 | 68.9957 | 79.6176
| TMY15 WA | 8220743 | 2177324 | 2701816 | 190691 | 2023218 | 2133001 | 25066 | 138978 | 345722 | 34299 | 1228691 | 17990858 | 84.8725 | variance | variance
| XMY Min WA | 18263742 | 1435496 | 2701816 | 188582 | 2023218 | 2504417 | 50302 | 91627 | 345722 | 34299 | 1228691 | 27639221 | 130.3891 | 64.86% | 16.73%
| XMY Max WA | 4555264 | 2644544 | 2701816 | 193406 | 2023218 | 1943529 | 14767 | 168801 | 345722 | 34299 | 1228691 | 14625366 | 68.9957
5B - Boulder | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 8595412 | 1548799 | 2701816 | 179448 | 2023218 | 2187705 | 27353 | 98860 | 345722 | 34299 | 1228691 | 17742632 | 83.7015 | max EUI | max EUI
| TMY3 DOE | 8138570 | 1543085 | 2701816 | 181775 | 2023218 | 2174139 | 26237 | 98495 | 345722 | 34299 | 1228691 | 17267356 | 81.4594 | 144.3001 | 90.201
| TMY3 WA | 9725858 | 1530639 | 2701816 | 182708 | 2023218 | 2318332 | 31171 | 97700 | 345722 | 34299 | 1228691 | 18991463 | 89.5929 | min EUI | min EUI
| TMY7 WA | 9840633 | 1546757 | 2701816 | 182795 | 2023218 | 2315260 | 31118 | 98729 | 345722 | 34299 | 1228691 | 19120347 | 90.201 | 70.8555 | 81.4594
| TMY15 WA | 9444077 | 1555338 | 2701816 | 182320 | 2023218 | 2299216 | 30366 | 99277 | 345722 | 34299 | 1228691 | 18715649 | 88.2918 | variance | variance
| XMY Min WA | 21146785 | 1298317 | 2701816 | 185905 | 2023218 | 2710880 | 58207 | 82871 | 345722 | 34299 | 1228691 | 30588020 | 144.3001 | 90.16% | 10.73%
| XMY Max WA | 5678238 | 1810275 | 2701816 | 180405 | 2023218 | 2110278 | 19788 | 115549 | 345722 | 34299 | 1228691 | 15019588 | 70.8555
5C - Vancouver | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| doeCWEC | 8044943 | 1012550 | 2701816 | 198924 | 2023218 | 2039819 | 23952 | 64631 | 345722 | 34299 | 702429 | 16489874 | 77.7916 | max EUI | max EUI
| CWEC | 8045646 | 1008979 | 2701816 | 197873 | 2023218 | 2039912 | 23983 | 64403 | 345722 | 34299 | 702429 | 16485851 | 77.7726 | 105.8828 | 79.1109
| TMY3 WA | 6439652 | 1084989 | 2701816 | 198124 | 2023218 | 1924974 | 19783 | 69255 | 345722 | 34299 | 702429 | 14841832 | 70.0169 | min EUI | min EUI
| TMY7 WA | 8319537 | 986094 | 2701816 | 200013 | 2023218 | 2071131 | 24764 | 62942 | 345722 | 34299 | 702429 | 16769536 | 79.1109 | 63.7746 | 70.0169
| TMY15 WA | 7432676 | 1013762 | 2701816 | 199782 | 2023218 | 2000029 | 22648 | 64708 | 345722 | 34299 | 702429 | 15838660 | 74.7195 | variance | variance
| XMY Min WA | 13815131 | 866220 | 2701816 | 194764 | 2023218 | 2370803 | 37242 | 55291 | 345722 | 34299 | 702429 | 22444506 | 105.8828 | 54.14% | 11.69%
| XMY Max WA | 5115213 | 1178089 | 2701816 | 201408 | 2023218 | 1827053 | 16602 | 75197 | 345722 | 34299 | 702429 | 13518617 | 63.7746
6A - Minneapolis | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 13337164 | 1817923 | 2701816 | 182007 | 2023218 | 2263043 | 38281 | 116038 | 345722 | 34299 | 1228691 | 22859511 | 107.8406 | max EUI | max EUI
| TMY3 DOE | 12843576 | 1766402 | 2701816 | 184378 | 2023218 | 2253010 | 38018 | 112749 | 345722 | 34299 | 1228691 | 22303188 | 105.2161 | 150.6281 | 107.8406
| TMY3 WA | 8772608 | 2112429 | 2701816 | 192587 | 2023218 | 2115877 | 27472 | 134836 | 345722 | 34299 | 1228691 | 18460864 | 87.0898 | min EUI | min EUI
| TMY7 WA | 11952051 | 1930124 | 2701816 | 192030 | 2023218 | 2254135 | 35744 | 123199 | 345722 | 34299 | 1228691 | 21592338 | 101.8627 | 77.2861 | 87.0898
| TMY15 WA | 10216755 | 2035089 | 2701816 | 192430 | 2023218 | 2181311 | 30940 | 129899 | 345722 | 34299 | 1228691 | 19891479 | 93.8388 | variance | variance
| XMY Min WA | 22625518 | 1307622 | 2701816 | 191010 | 2023218 | 2555439 | 61280 | 83465 | 345722 | 34299 | 1228691 | 31929389 | 150.6281 | 69.71% | 19.72%
| XMY Max WA | 6024219 | 2793858 | 2701816 | 193137 | 2023218 | 2068417 | 19701 | 178331 | 345722 | 34299 | 1228691 | 16382718 | 77.2861
6B - Helena | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 12093262 | 1214541 | 2701816 | 181619 | 2023218 | 2211528 | 38118 | 77524 | 345722 | 34299 | 1228691 | 20921647 | 98.6987 | max EUI | max EUI
| TMY3 DOE | 11593479 | 1226360 | 2701816 | 183183 | 2023218 | 2215768 | 37164 | 78278 | 345722 | 34299 | 1228691 | 20439287 | 96.4231 | 161.1282 | 98.6987
| TMY3 WA | 10534030 | 1538387 | 2701816 | 187769 | 2023218 | 2287169 | 35095 | 98195 | 345722 | 34299 | 1228691 | 19785700 | 93.3398 | min EUI | min EUI
| TMY7 WA | 918637 | 6374902 | 2701816 | 184134 | 2023218 | 1945740 | 2384 | 406909 | 345722 | 34299 | 1228691 | 14937761 | 70.4694 | 70.4694 | 70.4694
| TMY15 WA | 11287146 | 1431173 | 2701816 | 187976 | 2023218 | 2297318 | 37056 | 91351 | 345722 | 34299 | 1228691 | 20437075 | 96.4127 | variance | variance
| XMY Min WA | 24850699 | 1144382 | 2701816 | 188683 | 2023218 | 2723822 | 69455 | 73046 | 345722 | 34299 | 1228691 | 34155142 | 161.1282 | 94.02% | 29.28%
| XMY Max WA | 7644854 | 1764943 | 2701816 | 185698 | 2023218 | 2124454 | 26616 | 112656 | 345722 | 34299 | 1228691 | 16964276 | 80.0296
7 - Duluth | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 16286989 | 1368783 | 2701816 | 181744 | 2023218 | 2414334 | 46862 | 87369 | 345722 | 34299 | 1228691 | 25491136 | 120.2554 | max EUI | max EUI
| TMY3 DOE | 15483600 | 1380401 | 2701816 | 184084 | 2023218 | 2381881 | 45196 | 88111 | 345722 | 34299 | 1228691 | 24668328 | 116.3738 | 158.2737 | 120.2554
| TMY3 WA | 10100956 | 1744915 | 2701816 | 195014 | 2023218 | 2211624 | 31831 | 111378 | 345722 | 34299 | 1228691 | 19500773 | 91.9956 | min EUI | min EUI
| TMY7 WA | 13022383 | 1638063 | 2701816 | 194789 | 2023218 | 2348249 | 39212 | 104557 | 345722 | 34299 | 1228691 | 22452308 | 105.9196 | 80.57 | 91.9956
| TMY15 WA | 11172005 | 1660417 | 2701816 | 193819 | 2023218 | 2250595 | 34447 | 105984 | 345722 | 34299 | 1228691 | 20522322 | 96.8148 | variance | variance
| XMY Min WA | 24235344 | 1208043 | 2701816 | 192124 | 2023218 | 2666822 | 65566 | 77109 | 345722 | 34299 | 1228691 | 33550063 | 158.2737 | 66.77% | 24.28%
| XMY Max WA | 7307783 | 2202738 | 2701816 | 197235 | 2023218 | 2101448 | 23967 | 140600 | 345722 | 34299 | 1228691 | 17078826 | 80.57
8 - Fairbanks | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 24755730 | 943896 | 2742519 | 202309 | 2023218 | 2556145 | 69136 | 60249 | 345722 | 34299 | 1228691 | 33733223 | 159.1377 | max EUI | max EUI
| TMY3 DOE | 22391785 | 963301 | 2742519 | 203529 | 2023218 | 2516242 | 64425 | 61487 | 345722 | 34299 | 1228691 | 31346527 | 147.8784 | 211.1911 | 159.1377
| TMY3 WA | 16517000 | 1161352 | 2742519 | 205713 | 2023218 | 2425071 | 51759 | 74129 | 345722 | 34299 | 1228691 | 25580782 | 120.6783 | min EUI | min EUI
| TMY7 WA | 20380107 | 1052578 | 2742519 | 205813 | 2023218 | 2527934 | 61402 | 67186 | 345722 | 34299 | 1228691 | 29440778 | 138.888 | 101.5961 | 120.6783
| TMY15 WA | 18759162 | 1111007 | 2742519 | 206163 | 2023218 | 2474358 | 56929 | 70915 | 345722 | 34299 | 1228691 | 27824292 | 131.2621 | variance | variance
| XMY Min WA | 35470914 | 910887 | 2742519 | 208685 | 2023218 | 2878958 | 93879 | 58142 | 345722 | 34299 | 1228691 | 44767223 | 211.1911 | 74.11% | 26.01%
| XMY Max WA | 12395496 | 1349946 | 2742519 | 205175 | 2023218 | 2311050 | 42232 | 86167 | 345722 | 34299 | 1228691 | 21535824 | 101.5961
1A - Miami
2A - Houston
2B - Phoenix
3A - Atlanta
3B - Las Vegas
3C - San Francisco
4A - Baltimore
4B - Albuquerque
4C - Portland
5A - Chicago
5B - Boulder
5C - Vancouver
6A - Minneapolis
6B - Helena
7 - Duluth
8 - Fairbanks

## 2s Additional Indicators
[15 empty] | Predicted Percentage Dissatisfied | [9 empty] | Peak Heating Load | [9 empty] | Peak Cooling Load
Climate Zone | Climate File | FLOOR 1 | Mech | FLOOR 2 | AUDITORIUM | GYM | KITCHEN CAFETERIA | Unmet Hours (Heating) | Unmet Hours (Cooling) | UH Compliance | Peak Heating Load | Peak Cooling Load | EUI |  | Climate | [9 empty] | Climate | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | Climate | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY7WA | 86 | 28 | 93 | 25 | 19 | 25 | 0 | 1 | 1 | 3658993 | 2270994 | aaa |  | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 1A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3658993 | 12:00, January | 3658993 | 12:00, January | 3658993 | 1A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 2378 | 23:30, May | 2270994 | 14:30, September | 830819
1A | TMY3WA | 91 | 32 | 95 | 29 | 21 | 28 | 1 | 29 | 30 | 3658993 | 2270994 | aaa | 1AFLOOR 1TMY7WA | 1A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 6 | 08:30,13/Feb | 100 | 16:30,10/Sep | 86 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY3 | 83 | 27 | 91 | 24 | 18 | 24 | 0 | 24 | 24 | 3658993 | 2270994 | aaa | 1AMECHTMY7WA | 1A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 04:30,29/Dec | 50 | 14:30,10/Sep | 28 | 2A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3817965 | 12:00, January | 3817965 | 12:00, January | 3817965 | 2A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 2027098 | 14:30, September | 682659
1A | TMY2 | 83 | 26 | 91 | 24 | 17 | 24 | 0 | 24 | 24 | 3658993 | 2270994 | aaa | 1AFLOOR 2TMY7WA | 1A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 15 | 10:30,03/Jan | 100 | 15:30,01/Mar | 93 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY15WA | 88 | 30 | 94 | 27 | 20 | 27 | 0 | 27 | 27 | 3658993 | 2270994 | aaa | 1AAUDITORIUMTMY7WA | 1A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 06:30,05/Jan | 68 | 15:30,18/Jul | 25 | 2B | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3335691 | 12:00, January | 3335691 | 12:00, January | 3335691 | 2B | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 25098 | 04:30, May | 2606043 | 13:30, September | 1129731
1A | MIN | 65 | 20 | 79 | 19 | 14 | 18 | 0 | 18 | 18 | 3658993 | 2270994 | aaa | 1AGYMTMY7WA | 1A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 08:30,12/Mar | 60 | 04:30,11/Sep | 19 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | MAX | 94 | 35 | 96 | 32 | 24 | 30 | 1 | 31 | 32 | 3658993 | 2270994 | aaa | 1AKITCHEN CAFETERIATMY7WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 13:30,02/Jan | 63 | 05:30,24/Jun | 25 | 3A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4088501 | 12:00, January | 4088501 | 12:00, January | 4088501 | 3A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1694811 | 14:30, September | 574493
2A | TMY7WA | 86 | 24 | 88 | 21 | 14 | 22 | 2 | 24 | 26 | 3817965 | 2027098 | aaa | 1AFLOOR 1TMY3WA | 1A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 32 | 07:30,23/Jan | 100 | 16:30,10/Sep | 91 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY3WA | 88 | 26 | 90 | 23 | 16 | 23 | 0 | 23 | 23 | 3817965 | 2027098 | aaa | 1AMECHTMY3WA | 1A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 06:30,23/Jan | 51 | 12:30,13/May | 32 | 3B | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3619627 | 12:00, January | 3619627 | 12:00, January | 3619627 | 3B | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 5842 | 03:30, May | 2270609 | 06:30, July | 921534
2A | TMY3 | 83 | 22 | 86 | 20 | 14 | 20 | 8 | 28 | 36 | 3817965 | 2027098 | aaa | 1AFLOOR 2TMY3WA | 1A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 60 | 00:30,01/Apr | 100 | 15:30,08/Mar | 95 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY2 | 83 | 22 | 85 | 19 | 13 | 20 | 2 | 22 | 24 | 3817965 | 2027098 | aaa | 1AAUDITORIUMTMY3WA | 1A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 05:30,22/Jan | 68 | 16:30,25/Jul | 29 | 3C | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3224919 | 12:00, January | 3224919 | 12:00, January | 3224919 | 3C | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1427049 | 14:30, September | 339168
2A | TMY15WA | 87 | 24 | 89 | 21 | 15 | 22 | 1 | 23 | 24 | 3817965 | 2027098 | aaa | 1AGYMTMY3WA | 1A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 08:30,14/Jan | 60 | 04:30,11/Sep | 21 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | MIN | 64 | 20 | 70 | 17 | 12 | 16 | 14 | 30 | 44 | 3817965 | 2027098 | aaa | 1AKITCHEN CAFETERIATMY3WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 6 | 16:30,23/Jan | 63 | 05:30,03/Jun | 28 | 4A | Heating plant sensible load | 46 rooms | RL_LPD.htg | Load (Btu/h) | 4186155 | 12:00, January | 4186155 | 12:00, January | 4186155 | 4A | Cooling plant sensible load | 46 rooms | RL_LPD.clg | Load (Btu/h) | 0 | 00:30, May | 1779127 | 14:30, September | 587015
2A | MAX | 95 | 31 | 95 | 27 | 18 | 27 | 3 | 30 | 33 | 3817965 | 2027098 | aaa | 1AFLOOR 1TMY3 | 1A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 6 | 05:30,04/Feb | 99 | 15:30,22/Sep | 83 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY7WA | 84 | 22 | 85 | 19 | 16 | 19 | 16 | 35 | 51 | 3335691 | 2606043 | aaa | 1AMECHTMY3 | 1A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 07:30,24/Jan | 46 | 14:30,09/Sep | 27 | 4B | Heating plant sensible load | 46 rooms | RL_LPD.htg | Load (Btu/h) | 3979021 | 12:00, January | 3979021 | 12:00, January | 3979021 | 4B | Cooling plant sensible load | 46 rooms | RL_LPD.clg | Load (Btu/h) | 0 | 00:30, May | 1563996 | 14:30, September | 471018
2B | TMY3WA | 86 | 24 | 87 | 21 | 17 | 21 | 17 | 38 | 55 | 3335691 | 2606043 | aaa | 1AFLOOR 2TMY3 | 1A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 25 | 05:30,04/Feb | 100 | 15:30,13/Apr | 91 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY3 | 86 | 24 | 88 | 21 | 18 | 21 | 18 | 39 | 57 | 3335691 | 2606043 | aaa | 1AAUDITORIUMTMY3 | 1A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 01:30,21/Jan | 66 | 10:30,07/Aug | 24 | 4C | Heating plant sensible load | 46 rooms | RL_LPD.htg | Load (Btu/h) | 3717432 | 12:00, January | 3717432 | 12:00, January | 3717432 | 4C | Cooling plant sensible load | 46 rooms | RL_LPD.clg | Load (Btu/h) | 0 | 00:30, May | 1647824 | 14:30, September | 523567
2B | TMY2 | 85 | 23 | 86 | 20 | 17 | 20 | 22 | 42 | 64 | 3335691 | 2606043 | aaa | 1AGYMTMY3 | 1A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,27/Dec | 59 | 03:30,09/Sep | 18 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY15WA | 84 | 23 | 85 | 20 | 16 | 20 | 17 | 37 | 54 | 3335691 | 2606043 | aaa | 1AKITCHEN CAFETERIATMY3 | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 08:30,27/Dec | 63 | 04:30,07/Jun | 24 | 5A | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 4783322 | 12:00, January | 4783322 | 12:00, January | 4783322 | 5A | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1715606 | 14:30, September | 547479
2B | MIN | 72 | 18 | 75 | 16 | 12 | 14 | 25 | 39 | 64 | 3335691 | 2606043 | aaa | 1AFLOOR 1TMY2 | 1A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 7 | 00:30,13/Jan | 99 | 16:30,01/Sep | 83 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | MAX | 89 | 27 | 89 | 22 | 20 | 23 | 8 | 31 | 39 | 3335691 | 2606043 | aaa | 1AMECHTMY2 | 1A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 04:30,14/Feb | 45 | 13:30,09/Sep | 26 | 5B | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4593129 | 12:00, January | 4593129 | 12:00, January | 4593129 | 5B | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1623303 | 14:30, September | 435957
3A | TMY7WA | 73 | 20 | 77 | 17 | 12 | 17 | 6 | 23 | 29 | 4088501 | 1694811 | aaa | 1AFLOOR 2TMY2 | 1A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 14 | 05:30,04/Jan | 100 | 13:30,14/May | 91 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY3WA | 77 | 20 | 81 | 17 | 12 | 18 | 5 | 23 | 28 | 4088501 | 1694811 | aaa | 1AAUDITORIUMTMY2 | 1A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 18:30,31/Jan | 67 | 10:30,22/May | 24 | 5C | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3909844 | 12:00, January | 3909844 | 12:00, January | 3909844 | 5C | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1097704 | 16:30, September | 244993
3A | TMY3 | 72 | 20 | 76 | 17 | 12 | 17 | 5 | 22 | 27 | 4088501 | 1694811 | aaa | 1AGYMTMY2 | 1A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 18:30,20/Mar | 58 | 01:30,27/Jun | 17 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY2 | 70 | 19 | 75 | 16 | 11 | 16 | 6 | 22 | 28 | 4088501 | 1694811 | aaa | 1AKITCHEN CAFETERIATMY2 | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 12:30,02/Jan | 64 | 04:30,21/May | 24 | 6A | Heating plant sensible load | 46 rooms | ROOMLOADS_TMY2.htg | Load (Btu/h) | 5063981 | 12:00, January | 5063981 | 12:00, January | 5063981 | 6A | Cooling plant sensible load | 46 rooms | ROOMLOADS_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1659937 | 14:30, September | 552584
3A | TMY15WA | 75 | 20 | 79 | 17 | 12 | 17 | 5 | 22 | 27 | 4088501 | 1694811 | aaa | 1AFLOOR 1TMY15WA | 1A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 6 | 04:30,11/Jan | 100 | 16:30,07/Oct | 88 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | MIN | 52 | 19 | 59 | 16 | 11 | 13 | 9 | 22 | 31 | 4088501 | 1694811 | aaa | 1AMECHTMY15WA | 1A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 06:30,12/Jan | 52 | 13:30,28/May | 30 | 6B | Heating plant sensible load | 46 rooms | ROOMLOAD_TMY2.htg | Load (Btu/h) | 5141729 | 12:00, January | 5141729 | 12:00, January | 5141729 | 6B | Cooling plant sensible load | 46 rooms | ROOMLOAD_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1535761 | 16:30, September | 413026
3A | MAX | 88 | 25 | 90 | 20 | 14 | 22 | 1 | 23 | 24 | 4088501 | 1694811 | aaa | 1AFLOOR 2TMY15WA | 1A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 25 | 06:30,09/Jan | 100 | 14:30,26/Mar | 94 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3B | TMY7WA | 77 | 20 | 80 | 17 | 15 | 17 | 10 | 27 | 37 | 3619627 | 2270609 | aaa | 1AAUDITORIUMTMY15WA | 1A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 05:30,12/Jan | 68 | 15:30,11/Jul | 27 | 7 | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 5145132 | 12:00, January | 5145132 | 12:00, January | 5145132 | 7 | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1362498 | 14:30, September | 385377
3B | TMY3WA | 79 | 21 | 81 | 18 | 15 | 18 | 12 | 30 | 42 | 3619627 | 2270609 | aaa | 1AGYMTMY15WA | 1A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,28/Dec | 59 | 07:30,29/Aug | 20 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3B | TMY3 | 78 | 20 | 80 | 18 | 16 | 18 | 18 | 36 | 54 | 3619627 | 2270609 | aaa | 1AKITCHEN CAFETERIATMY15WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 13:30,09/Jan | 62 | 03:30,27/Aug | 27 | 8 | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 5939305 | 12:00, January | 5939305 | 12:00, January | 5939305 | 8 | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1242278 | 16:30, May | 294945
3B | TMY2 | 78 | 20 | 80 | 18 | 15 | 17 | 13 | 30 | 43 | 3619627 | 2270609 | aaa | 1AFLOOR 1MIN | 1A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 03:30,28/Mar | 99 | 16:30,08/Sep | 65
3B | TMY15WA | 77 | 20 | 80 | 18 | 15 | 17 | 11 | 28 | 39 | 3619627 | 2270609 | aaa | 1AMECHMIN | 1A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 05:30,06/Dec | 49 | 15:30,08/Sep | 20
3B | MIN | 61 | 19 | 66 | 15 | 12 | 13 | 15 | 28 | 43 | 3619627 | 2270609 | aaa | 1AFLOOR 2MIN | 1A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 6 | 15:30,24/Jan | 100 | 15:30,28/Apr | 79
3B | MAX | 84 | 23 | 85 | 19 | 17 | 20 | 3 | 23 | 26 | 3619627 | 2270609 | aaa | 1AAUDITORIUMMIN | 1A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 12:30,18/Jan | 66 | 09:30,25/Jul | 19
3C | TMY7WA | 64 | 8 | 72 | 7 | 7 | 9 | 1 | 10 | 11 | 3224919 | 1427049 | aaa | 1AGYMMIN | 1A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,07/Nov | 56 | 22:30,25/Jul | 14
3C | TMY3WA | 71 | 11 | 77 | 9 | 8 | 12 | 2 | 14 | 16 | 3224919 | 1427049 | aaa | 1AKITCHEN CAFETERIAMIN | 1A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 20:30,12/Jan | 63 | 06:30,07/Aug | 18
3C | TMY3 | 66 | 9 | 73 | 8 | 7 | 10 | 10 | 20 | 30 | 3224919 | 1427049 | aaa | 1AFLOOR 1MAX | 1A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 77 | 07:30,15/Jan | 100 | 15:30,01/Sep | 94
3C | TMY2 | 63 | 9 | 70 | 8 | 8 | 9 | 0 | 9 | 9 | 3224919 | 1427049 | aaa | 1AMECHMAX | 1A | People dissatisfied | MECH | MAX | Percentage (%) | 17 | 08:30,16/Jan | 55 | 14:30,03/Sep | 35
3C | TMY15WA | 67 | 9 | 74 | 8 | 8 | 11 | 2 | 13 | 15 | 3224919 | 1427049 | aaa | 1AFLOOR 2MAX | 1A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 85 | 01:30,18/Apr | 100 | 16:30,05/Mar | 96
3C | MIN | 53 | 9 | 61 | 9 | 8 | 7 | 24 | 31 | 55 | 3224919 | 1427049 | aaa | 1AAUDITORIUMMAX | 1A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 6 | 12:30,15/Jan | 68 | 14:30,15/Aug | 32
3C | MAX | 76 | 14 | 81 | 11 | 9 | 15 | 0 | 15 | 15 | 3224919 | 1427049 | aaa | 1AGYMMAX | 1A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,04/Dec | 61 | 04:30,22/Sep | 24
4A | TMY7WA LPD | 247 | 13 | 362 | 21 | 45 | 62 | 120 | 182 | 302 | 4186155 | 1779127 | aaa | 1AKITCHEN CAFETERIAMAX | 1A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 7 | 08:30,15/Jan | 63 | 04:30,21/Oct | 30
4A | TMY3WA LPD | 247 | 13 | 364 | 20 | 44 | 59 | 100 | 159 | 259 | 4186155 | 1779127 | aaa | 2ALocationFilename | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
4A | TMY3 LPD | 260 | 13 | 375 | 22 | 46 | 66 | 173 | 239 | 412 | 4186155 | 1779127 | aaa | 2AFLOOR 1TMY7WA | 2A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 21 | 06:30,17/Jan | 100 | 16:30,13/Sep | 86
4A | TMY2 LPD | 263 | 13 | 377 | 23 | 47 | 68 | 101 | 169 | 270 | 4186155 | 1779127 | aaa | 2AMECHTMY7WA | 2A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 02:30,02/Mar | 47 | 14:30,28/May | 24
4A | MIN LPD | 296 | 12 | 399 | 32 | 54 | 91 | 153 | 244 | 397 | 4186155 | 1779127 | aaa | 2AFLOOR 2TMY7WA | 2A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 21 | 06:30,17/Jan | 100 | 14:30,09/Apr | 88
4A | TMY15WA LPD | 248 | 13 | 367 | 20 | 44 | 60 | 164 | 224 | 388 | 4186155 | 1779127 | aaa | 2AAUDITORIUMTMY7WA | 2A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 07:30,03/Mar | 67 | 16:30,18/Jul | 21
4A | MAX LPD | 244 | 12 | 365 | 16 | 40 | 49 | 60 | 109 | 169 | 4186155 | 1779127 | aaa | 2AGYMTMY7WA | 2A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 11:30,27/Feb | 57 | 01:30,16/Aug | 14
4B | TMY7WA LPD | 13 | 20 | 15 | 15 | 14 | 12 | 1162 | 1174 | 2336 | 3979021 | 1563996 | aaa | 2AKITCHEN CAFETERIATMY7WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 15:30,11/Dec | 64 | 07:30,29/Aug | 22
4B | TMY3WA LPD | 13 | 21 | 15 | 14 | 16 | 12 | 1218 | 1230 | 2448 | 3979021 | 1563996 | aaa | 2AFLOOR 1TMY3WA | 2A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 7 | 05:30,21/Dec | 100 | 16:30,28/Sep | 88
4B | TMY3 LPD | 14 | 21 | 16 | 15 | 15 | 13 | 1710 | 1723 | 3433 | 3979021 | 1563996 | aaa | 2AMECHTMY3WA | 2A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 08:30,02/Dec | 53 | 15:30,20/Sep | 26
4B | TMY2 LPD | 14 | 20 | 16 | 15 | 15 | 13 | 1479 | 1492 | 2971 | 3979021 | 1563996 | aaa | 2AFLOOR 2TMY3WA | 2A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 8 | 06:30,20/Dec | 100 | 15:30,24/Mar | 90
4B | MIN LPD | 15 | 20 | 16 | 16 | 12 | 12 | 1709 | 1721 | 3430 | 3979021 | 1563996 | aaa | 2AAUDITORIUMTMY3WA | 2A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 13:30,16/Jan | 67 | 14:30,22/Aug | 23
4B | TMY15WA LPD | 13 | 20 | 16 | 15 | 15 | 12 | 2285 | 2297 | 4582 | 3979021 | 1563996 | aaa | 2AGYMTMY3WA | 2A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 14:30,23/Jan | 58 | 04:30,28/Sep | 16
4B | MAX LPD | 14 | 24 | 16 | 15 | 19 | 13 | 457 | 470 | 927 | 3979021 | 1563996 | aaa | 2AKITCHEN CAFETERIATMY3WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 12:30,25/Dec | 65 | 05:30,07/Jul | 23
4C | TMY7WA LPD | 11 | 14 | 13 | 12 | 10 | 9 | 75 | 84 | 159 | 3717432 | 1647824 | aaa | 2AFLOOR 1TMY3 | 2A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 21 | 05:30,15/Feb | 100 | 15:30,03/Aug | 83
4C | TMY3WA LPD | 10 | 12 | 12 | 11 | 9 | 9 | 56 | 65 | 121 | 3717432 | 1647824 | aaa | 2AMECHTMY3 | 2A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 00:30,11/Nov | 44 | 14:30,05/Jul | 22
4C | TMY3 LPD | 11 | 13 | 13 | 11 | 9 | 10 | 171 | 181 | 352 | 3717432 | 1647824 | aaa | 2AFLOOR 2TMY3 | 2A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 19 | 05:30,12/Feb | 100 | 15:30,29/Apr | 86
4C | TMY2 LPD | 11 | 13 | 13 | 11 | 9 | 10 | 220 | 230 | 450 | 3717432 | 1647824 | aaa | 2AAUDITORIUMTMY3 | 2A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 02:30,01/Dec | 66 | 14:30,07/Aug | 20
4C | MIN LPD | 14 | 18 | 15 | 15 | 10 | 10 | 209 | 219 | 428 | 3717432 | 1647824 | aaa | 2AGYMTMY3 | 2A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 14:30,26/Dec | 55 | 23:30,01/Aug | 14
4C | TMY15WA LPD | 11 | 13 | 13 | 12 | 9 | 9 | 815 | 824 | 1639 | 3717432 | 1647824 | aaa | 2AKITCHEN CAFETERIATMY3 | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 11:30,06/Feb | 64 | 07:30,20/Jun | 20
4C | MAX LPD | 12 | 15 | 14 | 12 | 12 | 12 | 0 | 12 | 12 | 3717432 | 1647824 | aaa | 2AFLOOR 1TMY2 | 2A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 8 | 05:30,15/Jan | 100 | 16:30,16/Sep | 83
5A | 5A_TMY7_WA | 15 | 21 | 17 | 16 | 11 | 14 | 69 | 83 | 152 | 4783322 | 1715606 | aaa | 2AMECHTMY2 | 2A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 03:30,28/Feb | 46 | 06:30,11/Jan | 22
5A | 5A_TMY3_WA | 15 | 21 | 17 | 16 | 11 | 14 | 56 | 70 | 126 | 4783322 | 1715606 | aaa | 2AFLOOR 2TMY2 | 2A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 8 | 06:30,11/Jan | 100 | 15:30,29/Apr | 85
5A | 5A_TMY3 | 15 | 21 | 17 | 16 | 11 | 14 | 84 | 98 | 182 | 4783322 | 1715606 | aaa | 2AAUDITORIUMTMY2 | 2A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 15:30,16/Feb | 66 | 10:30,17/Jul | 19
5A | 5A_TMY2 | 15 | 20 | 17 | 16 | 11 | 14 | 57 | 71 | 128 | 4783322 | 1715606 | aaa | 2AGYMTMY2 | 2A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 10:30,14/Feb | 51 | 22:30,18/Jul | 13
5A | 5A_TMY15_WA | 15 | 22 | 17 | 16 | 11 | 14 | 76 | 90 | 166 | 4783322 | 1715606 | aaa | 2AKITCHEN CAFETERIATMY2 | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 19:30,12/Jan | 65 | 07:30,04/Jul | 20
5A | 5A_MIN_WA | 16 | 19 | 16 | 16 | 11 | 12 | 130 | 142 | 272 | 4783322 | 1715606 | aaa | 2AFLOOR 1TMY15WA | 2A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 29 | 05:30,30/Dec | 100 | 16:30,13/Sep | 87
5A | 5A_MAX_WA | 17 | 26 | 19 | 17 | 12 | 17 | 0 | 17 | 17 | 4783322 | 1715606 | aaa | 2AMECHTMY15WA | 2A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 00:30,04/Mar | 46 | 14:30,14/Sep | 24
5B | TMY7WA | 14 | 17 | 15 | 15 | 12 | 11 | 1031 | 1042 | 2073 | 4593129 | 1623303 | aaa | 2AFLOOR 2TMY15WA | 2A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 25 | 04:30,27/Dec | 100 | 12:30,22/Apr | 89
5B | TMY3WA | 13 | 17 | 15 | 14 | 12 | 11 | 1051 | 1062 | 2113 | 4593129 | 1623303 | aaa | 2AAUDITORIUMTMY15WA | 2A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 19:30,28/Feb | 67 | 14:30,22/Aug | 21
5B | TMY3 | 14 | 19 | 15 | 14 | 14 | 12 | 789 | 801 | 1590 | 4593129 | 1623303 | aaa | 2AGYMTMY15WA | 2A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 13:30,10/Jan | 57 | 01:30,16/Aug | 15
5B | TMY2 | 14 | 19 | 15 | 15 | 13 | 12 | 810 | 822 | 1632 | 4593129 | 1623303 | aaa | 2AKITCHEN CAFETERIATMY15WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 15:30,11/Dec | 64 | 07:30,06/Jun | 22
5B | TMY15WA | 13 | 17 | 15 | 14 | 12 | 11 | 864 | 875 | 1739 | 4593129 | 1623303 | aaa | 2AFLOOR 1MIN | 2A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 7 | 17:30,08/Feb | 99 | 16:30,29/Jul | 64
5B | MIN | 18 | 21 | 18 | 18 | 13 | 13 | 1651 | 1664 | 3315 | 4593129 | 1623303 | aaa | 2AMECHMIN | 2A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 05:30,02/Apr | 51 | 08:30,10/Jan | 20
5B | MAX | 13 | 20 | 15 | 13 | 14 | 11 | 77 | 88 | 165 | 4593129 | 1623303 | aaa | 2AFLOOR 2MIN | 2A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 7 | 18:30,13/Feb | 100 | 16:30,24/May | 70
5C | TMY7WA | 11 | 12 | 12 | 11 | 9 | 8 | 10 | 18 | 28 | 3909844 | 1097704 | aaa | 2AAUDITORIUMMIN | 2A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 14:30,08/Mar | 68 | 18:30,18/Jul | 17
5C | TMY3WA | 10 | 11 | 12 | 11 | 9 | 9 | 16 | 25 | 41 | 3909844 | 1097704 | aaa | 2AGYMMIN | 2A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 15:30,04/Apr | 48 | 19:30,13/Jun | 12
5C | TMY2 | 15 | 19 | 17 | 16 | 11 | 13 | 114 | 127 | 241 | 3909844 | 1097704 | aaa | 2AKITCHEN CAFETERIAMIN | 2A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 18:30,03/Mar | 62 | 05:30,09/Aug | 16
5C | TMY15WA | 10 | 11 | 12 | 11 | 9 | 8 | 24 | 32 | 56 | 3909844 | 1097704 | aaa | 2AFLOOR 1MAX | 2A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 72 | 00:30,18/Jan | 100 | 16:30,31/May | 95
5C | MIN | 14 | 16 | 14 | 15 | 10 | 9 | 25 | 34 | 59 | 3909844 | 1097704 | aaa | 2AMECHMAX | 2A | People dissatisfied | MECH | MAX | Percentage (%) | 8 | 00:30,18/Jan | 61 | 15:30,03/Sep | 31
5C | MAX | 10 | 13 | 13 | 11 | 9 | 10 | 324 | 334 | 658 | 3909844 | 1097704 | aaa | 2AFLOOR 2MAX | 2A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 70 | 00:30,18/Jan | 100 | 14:30,29/Mar | 95
5C | doeCWEC | 11 | 12 | 12 | 11 | 9 | 9 | 0 | 9 | 9 | 3909844 | 1097704 | aaa | 2AAUDITORIUMMAX | 2A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 6 | 11:30,30/Dec | 68 | 13:30,08/Aug | 27
5C | CWEC | 11 | 12 | 12 | 11 | 9 | 9 | 63 | 72 | 135 | 5063981 | 1659937 | aaa | 2AGYMMAX | 2A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 11:30,26/Dec | 58 | 02:30,02/Sep | 18
6A | TMY7WA | 15 | 21 | 17 | 16 | 11 | 14 | 120 | 134 | 254 | 5063981 | 1659937 | aaa | 2AKITCHEN CAFETERIAMAX | 2A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 6 | 09:30,16/Jan | 63 | 05:30,02/Oct | 27
6A | TMY3WA | 15 | 21 | 17 | 16 | 11 | 14 | 151 | 165 | 316 | 5063981 | 1659937 | aaa | 2BLocationFilename | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
6A | TMY3 | 16 | 21 | 18 | 17 | 12 | 14 | 140 | 154 | 294 | 5063981 | 1659937 | aaa | 2BFLOOR 1TMY7WA | 2B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 35 | 05:30,27/Dec | 100 | 16:30,10/Aug | 84
6A | TMY2 | 16 | 21 | 18 | 16 | 12 | 14 | 202 | 216 | 418 | 5063981 | 1659937 | aaa | 2BMECHTMY7WA | 2B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 08:30,17/Jan | 53 | 14:30,10/Aug | 22
6A | TMY15WA | 15 | 22 | 17 | 16 | 12 | 14 | 403 | 417 | 820 | 5063981 | 1659937 | aaa | 2BFLOOR 2TMY7WA | 2B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 31 | 05:30,27/Dec | 100 | 14:30,12/May | 85
6A | MIN | 17 | 21 | 18 | 17 | 12 | 13 | 79 | 92 | 171 | 5063981 | 1659937 | aaa | 2BAUDITORIUMTMY7WA | 2B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 01:30,24/Nov | 63 | 13:30,11/Jul | 19
6A | MAX | 18 | 29 | 20 | 18 | 14 | 17 | 675 | 692 | 1367 | 5141729 | 1535761 | aaa | 2BGYMTMY7WA | 2B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 14:30,18/Dec | 56 | 05:30,16/Aug | 16
6B | TMY7WA | 36 | 65 | 37 | 37 | 22 | 38 | 621 | 659 | 1280 | 5141729 | 1535761 | aaa | 2BKITCHEN CAFETERIATMY7WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 20:30,30/Dec | 61 | 03:30,23/Aug | 19
6B | TMY3WA | 14 | 18 | 15 | 15 | 13 | 11 | 910 | 921 | 1831 | 5141729 | 1535761 | aaa | 2BFLOOR 1TMY3WA | 2B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 40 | 05:30,03/Dec | 100 | 15:30,26/Jul | 86
6B | TMY3 | 13 | 18 | 15 | 14 | 12 | 11 | 2140 | 2151 | 4291 | 5141729 | 1535761 | aaa | 2BMECHTMY3WA | 2B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 05:30,05/Mar | 53 | 13:30,09/Sep | 24
6B | TMY2 | 14 | 18 | 15 | 15 | 12 | 11 | 771 | 782 | 1553 | 5141729 | 1535761 | aaa | 2BFLOOR 2TMY3WA | 2B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 36 | 05:30,03/Dec | 100 | 14:30,10/May | 87
6B | TMY15WA | 13 | 17 | 15 | 14 | 12 | 10 | 1475 | 1485 | 2960 | 5141729 | 1535761 | aaa | 2BAUDITORIUMTMY3WA | 2B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 23:30,18/Dec | 62 | 12:30,22/Aug | 21
6B | MIN | 18 | 23 | 19 | 19 | 13 | 14 | 72 | 86 | 158 | 5141729 | 1535761 | aaa | 2BGYMTMY3WA | 2B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 16:30,11/Dec | 56 | 18:30,25/Jul | 17
6B | MAX | 13 | 20 | 15 | 14 | 15 | 11 | 44 | 55 | 99 | 5145132 | 1362498 | aaa | 2BKITCHEN CAFETERIATMY3WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 08:30,15/Jan | 61 | 07:30,26/Sep | 21
7 | TMY7WA | 15 | 19 | 16 | 15 | 11 | 13 | 49 | 62 | 111 | 5145132 | 1362498 | aaa | 2BFLOOR 1TMY3 | 2B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 45 | 05:30,14/Dec | 100 | 16:30,10/Aug | 86
7 | TMY3WA | 14 | 18 | 16 | 15 | 11 | 12 | 126 | 138 | 264 | 5145132 | 1362498 | aaa | 2BMECHTMY3 | 2B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 01:30,03/Jan | 53 | 13:30,03/Sep | 24
7 | TMY3 | 15 | 19 | 16 | 16 | 11 | 12 | 93 | 105 | 198 | 5145132 | 1362498 | aaa | 2BFLOOR 2TMY3 | 2B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 43 | 07:30,31/Jan | 100 | 14:30,12/May | 88
7 | TMY2 | 15 | 19 | 16 | 16 | 11 | 12 | 77 | 89 | 166 | 5145132 | 1362498 | aaa | 2BAUDITORIUMTMY3 | 2B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 21:30,05/Jan | 66 | 12:30,18/Jul | 21
7 | TMY15WA | 14 | 18 | 16 | 15 | 11 | 13 | 242 | 255 | 497 | 5145132 | 1362498 | aaa | 2BGYMTMY3 | 2B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,12/Dec | 56 | 06:30,10/Jul | 18
7 | MIN | 17 | 21 | 18 | 18 | 12 | 13 | 19 | 32 | 51 | 5145132 | 1362498 | aaa | 2BKITCHEN CAFETERIATMY3 | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 16:30,30/Jan | 60 | 02:30,30/Jul | 21
7 | MAX | 16 | 24 | 18 | 16 | 12 | 15 | 80 | 95 | 175 | 5939305 | 1242278 | aaa | 2BFLOOR 1TMY2 | 2B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 29 | 05:30,23/Dec | 100 | 16:30,16/Jul | 85
8 | TMY7WA | 16 | 20 | 17 | 16 | 12 | 13 | 132 | 145 | 277 | 5939305 | 1242278 | aaa | 2BMECHTMY2 | 2B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 03:30,07/Dec | 51 | 14:30,10/Sep | 23
8 | TMY3WA | 15 | 20 | 17 | 16 | 12 | 12 | 441 | 453 | 894 | 5939305 | 1242278 | aaa | 2BFLOOR 2TMY2 | 2B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 24 | 05:30,23/Dec | 100 | 15:30,20/May | 86
8 | TMY3 | 16 | 21 | 18 | 17 | 12 | 14 | 246 | 260 | 506 | 5939305 | 1242278 | aaa | 2BAUDITORIUMTMY2 | 2B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 10:30,05/Feb | 63 | 15:30,25/Jul | 20
8 | TMY2 | 17 | 21 | 18 | 18 | 12 | 14 | 418 | 432 | 850 | 5939305 | 1242278 | aaa | 2BGYMTMY2 | 2B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 12:30,20/Feb | 57 | 18:30,11/Jul | 17
8 | TMY15WA | 16 | 20 | 17 | 16 | 12 | 13 | 955 | 968 | 1923 | 5939305 | 1242278 | aaa | 2BKITCHEN CAFETERIATMY2 | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 08:30,04/Jan | 60 | 05:30,29/Jul | 20
8 | MIN | 21 | 26 | 21 | 22 | 14 | 16 | 0 | 16 | 16 | 5939305 | 1242278 | aaa | 2BFLOOR 1TMY15WA | 2B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 33 | 05:30,28/Dec | 100 | 15:30,26/Jul | 84
8 | MAX | 15 | 20 | 17 | 15 | 14 | 12 |  |  | 0 | 5939305 | 1242278 | aaa | 2BMECHTMY15WA | 2B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 06:30,05/Mar | 53 | 13:30,19/Jul | 23
[14 empty] | 2BFLOOR 2TMY15WA | 2B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 29 | 05:30,27/Dec | 100 | 13:30,21/May | 85
[14 empty] | 2BAUDITORIUMTMY15WA | 2B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 10:30,15/Feb | 61 | 13:30,01/Aug | 20
[14 empty] | 2BGYMTMY15WA | 2B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 15:30,25/Dec | 56 | 18:30,25/Jul | 16
[14 empty] | 2BKITCHEN CAFETERIATMY15WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 13:30,19/Dec | 60 | 05:30,31/Jul | 20
[14 empty] | 2BFLOOR 1MIN | 2B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 22 | 05:30,03/Feb | 100 | 11:30,07/Sep | 72
[14 empty] | 2BMECHMIN | 2B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 02:30,27/Mar | 47 | 14:30,06/Sep | 18
[14 empty] | 2BFLOOR 2MIN | 2B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 19 | 05:30,03/Feb | 100 | 14:30,27/Jul | 75
[14 empty] | 2BAUDITORIUMMIN | 2B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 10:30,12/Nov | 60 | 15:30,11/Jul | 16
[14 empty] | 2BGYMMIN | 2B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 09:30,14/Mar | 51 | 05:30,20/Jul | 12
[14 empty] | 2BKITCHEN CAFETERIAMIN | 2B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 19:30,26/Jan | 59 | 05:30,08/Sep | 14
[14 empty] | 2BFLOOR 1MAX | 2B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 57 | 07:30,27/Dec | 100 | 16:30,01/Sep | 89
[14 empty] | 2BMECHMAX | 2B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 06:30,28/Dec | 58 | 14:30,08/Sep | 27
[14 empty] | 2BFLOOR 2MAX | 2B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 57 | 07:30,26/Dec | 100 | 15:30,20/Apr | 89
[14 empty] | 2BAUDITORIUMMAX | 2B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 06:30,19/Dec | 62 | 13:30,11/Jul | 22
[14 empty] | 2BGYMMAX | 2B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 09:30,16/Jan | 56 | 02:30,04/Sep | 20
[14 empty] | 2BKITCHEN CAFETERIAMAX | 2B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 08:30,16/Dec | 56 | 17:30,25/Jul | 23
[14 empty] | 3ALocationFilename | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 3AFLOOR 1TMY7WA | 3A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 8 | 06:30,08/Feb | 99 | 16:30,12/Jul | 73
[14 empty] | 3AMECHTMY7WA | 3A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 02:30,24/Oct | 49 | 14:30,06/Sep | 20
[14 empty] | 3AFLOOR 2TMY7WA | 3A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 9 | 14:30,07/Feb | 100 | 15:30,06/May | 77
[14 empty] | 3AAUDITORIUMTMY7WA | 3A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 20:30,23/Oct | 65 | 14:30,01/Aug | 17
[14 empty] | 3AGYMTMY7WA | 3A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 12:30,04/Dec | 51 | 04:30,26/Jul | 12
[14 empty] | 3AKITCHEN CAFETERIATMY7WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 19:30,05/Feb | 61 | 01:30,16/Aug | 17
[14 empty] | 3AFLOOR 1TMY3WA | 3A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 21 | 06:30,26/Feb | 99 | 15:30,26/Jul | 77
[14 empty] | 3AMECHTMY3WA | 3A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 23:30,04/Nov | 45 | 14:30,18/May | 20
[14 empty] | 3AFLOOR 2TMY3WA | 3A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 19 | 06:30,26/Feb | 100 | 14:30,13/May | 81
[14 empty] | 3AAUDITORIUMTMY3WA | 3A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 10:30,27/Dec | 65 | 13:30,05/Sep | 17
[14 empty] | 3AGYMTMY3WA | 3A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 16:30,06/Nov | 47 | 20:30,27/Jun | 12
[14 empty] | 3AKITCHEN CAFETERIATMY3WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 15:30,21/Feb | 65 | 05:30,19/Jul | 18
[14 empty] | 3AFLOOR 1TMY3 | 3A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 7 | 05:30,16/Feb | 99 | 13:30,09/Sep | 72
[14 empty] | 3AMECHTMY3 | 3A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 06:30,27/Feb | 42 | 14:30,09/Sep | 20
[14 empty] | 3AFLOOR 2TMY3 | 3A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 8 | 16:30,14/Feb | 100 | 15:30,06/Jul | 76
[14 empty] | 3AAUDITORIUMTMY3 | 3A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 21:30,31/Dec | 64 | 11:30,15/Aug | 17
[14 empty] | 3AGYMTMY3 | 3A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 13:30,04/Feb | 42 | 20:30,13/Jun | 12
[14 empty] | 3AKITCHEN CAFETERIATMY3 | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 19:30,04/Jan | 59 | 01:30,09/Aug | 17
[14 empty] | 3AFLOOR 1TMY2 | 3A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 7 | 05:30,20/Jan | 99 | 16:30,02/Jul | 70
[14 empty] | 3AMECHTMY2 | 3A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 23:30,08/Apr | 40 | 15:30,10/Sep | 19
[14 empty] | 3AFLOOR 2TMY2 | 3A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 7 | 18:30,03/Jan | 100 | 15:30,02/Jul | 75
[14 empty] | 3AAUDITORIUMTMY2 | 3A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 09:30,25/Nov | 65 | 12:30,31/Jul | 16
[14 empty] | 3AGYMTMY2 | 3A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 12:30,24/Jan | 44 | 21:30,03/Jul | 11
[14 empty] | 3AKITCHEN CAFETERIATMY2 | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 19:30,15/Nov | 61 | 07:30,04/Jul | 16
[14 empty] | 3AFLOOR 1TMY15WA | 3A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 14 | 06:30,08/Feb | 99 | 16:30,12/Jul | 75
[14 empty] | 3AMECHTMY15WA | 3A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 00:30,11/Nov | 44 | 14:30,01/Aug | 20
[14 empty] | 3AFLOOR 2TMY15WA | 3A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 15 | 06:30,08/Feb | 100 | 14:30,20/May | 79
[14 empty] | 3AAUDITORIUMTMY15WA | 3A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 13:30,30/Oct | 65 | 14:30,01/Aug | 17
[14 empty] | 3AGYMTMY15WA | 3A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 12:30,27/Nov | 51 | 04:30,26/Jul | 12
[14 empty] | 3AKITCHEN CAFETERIATMY15WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 20:30,08/Feb | 61 | 01:30,16/Aug | 17
[14 empty] | 3AFLOOR 1MIN | 3A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 7 | 07:30,22/Feb | 97 | 16:30,09/Aug | 52
[14 empty] | 3AMECHMIN | 3A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 02:30,20/May | 47 | 08:30,24/Jan | 19
[14 empty] | 3AFLOOR 2MIN | 3A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 8 | 18:30,14/Mar | 100 | 16:30,10/Sep | 59
[14 empty] | 3AAUDITORIUMMIN | 3A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 02:30,22/May | 56 | 16:30,29/Aug | 16
[14 empty] | 3AGYMMIN | 3A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 14:30,18/Feb | 41 | 06:30,24/Jan | 11
[14 empty] | 3AKITCHEN CAFETERIAMIN | 3A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 19:30,26/Mar | 48 | 00:30,12/Jul | 13
[14 empty] | 3AFLOOR 1MAX | 3A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 43 | 04:30,27/Dec | 100 | 15:30,30/Jun | 88
[14 empty] | 3AMECHMAX | 3A | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 07:30,18/Jan | 47 | 16:30,30/Jun | 25
[14 empty] | 3AFLOOR 2MAX | 3A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 37 | 07:30,07/Feb | 100 | 15:30,29/Apr | 90
[14 empty] | 3AAUDITORIUMMAX | 3A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 23:30,28/Dec | 64 | 15:30,01/Aug | 20
[14 empty] | 3AGYMMAX | 3A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,23/Jan | 54 | 20:30,01/Aug | 14
[14 empty] | 3AKITCHEN CAFETERIAMAX | 3A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 15:30,26/Dec | 60 | 07:30,25/Jul | 22
[14 empty] | 3BLocationFilename | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 3BFLOOR 1TMY7WA | 3B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 23 | 05:30,06/Jan | 99 | 16:30,17/Sep | 77
[14 empty] | 3BMECHTMY7WA | 3B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 23:30,14/Nov | 48 | 13:30,06/Sep | 20
[14 empty] | 3BFLOOR 2TMY7WA | 3B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 20 | 05:30,05/Jan | 100 | 15:30,13/May | 80
[14 empty] | 3BAUDITORIUMTMY7WA | 3B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 08:30,06/Mar | 58 | 12:30,11/Jul | 17
[14 empty] | 3BGYMTMY7WA | 3B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 21:30,11/Jan | 52 | 01:30,14/Jul | 15
[14 empty] | 3BKITCHEN CAFETERIATMY7WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 20:30,22/Dec | 56 | 07:30,11/Jul | 17
[14 empty] | 3BFLOOR 1TMY3WA | 3B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 23 | 05:30,06/Dec | 99 | 16:30,17/Sep | 79
[14 empty] | 3BMECHTMY3WA | 3B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 23:30,14/Nov | 49 | 14:30,12/Aug | 21
[14 empty] | 3BFLOOR 2TMY3WA | 3B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 24 | 05:30,24/Dec | 100 | 13:30,07/May | 81
[14 empty] | 3BAUDITORIUMTMY3WA | 3B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 00:30,28/Feb | 58 | 12:30,11/Jul | 18
[14 empty] | 3BGYMTMY3WA | 3B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 11:30,10/Jan | 52 | 01:30,13/Aug | 15
[14 empty] | 3BKITCHEN CAFETERIATMY3WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 14:30,30/Jan | 57 | 06:30,22/Aug | 18
[14 empty] | 3BFLOOR 1TMY3 | 3B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 25 | 05:30,16/Feb | 100 | 15:30,05/Jul | 78
[14 empty] | 3BMECHTMY3 | 3B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 00:30,17/Mar | 50 | 14:30,02/Sep | 20
[14 empty] | 3BFLOOR 2TMY3 | 3B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 22 | 05:30,16/Feb | 100 | 15:30,03/May | 80
[14 empty] | 3BAUDITORIUMTMY3 | 3B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 12:30,19/Feb | 61 | 12:30,08/Aug | 18
[14 empty] | 3BGYMTMY3 | 3B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,10/Jan | 53 | 01:30,02/Sep | 16
[14 empty] | 3BKITCHEN CAFETERIATMY3 | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 19:30,08/Feb | 57 | 05:30,08/Jul | 18
[14 empty] | 3BFLOOR 1TMY2 | 3B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 15 | 05:30,11/Jan | 100 | 14:30,05/Aug | 78
[14 empty] | 3BMECHTMY2 | 3B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 23:30,20/Nov | 50 | 14:30,02/Sep | 20
[14 empty] | 3BFLOOR 2TMY2 | 3B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 19 | 05:30,11/Jan | 100 | 14:30,18/May | 80
[14 empty] | 3BAUDITORIUMTMY2 | 3B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 10:30,18/Feb | 59 | 12:30,07/Aug | 18
[14 empty] | 3BGYMTMY2 | 3B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 09:30,04/Mar | 54 | 21:30,08/Aug | 15
[14 empty] | 3BKITCHEN CAFETERIATMY2 | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 17:30,29/Dec | 55 | 05:30,05/Jul | 17
[14 empty] | 3BFLOOR 1TMY15WA | 3B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 23 | 05:30,05/Jan | 99 | 15:30,03/Sep | 77
[14 empty] | 3BMECHTMY15WA | 3B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 23:30,14/Nov | 50 | 13:30,03/Sep | 20
[14 empty] | 3BFLOOR 2TMY15WA | 3B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 21 | 05:30,05/Jan | 100 | 14:30,05/Jul | 80
[14 empty] | 3BAUDITORIUMTMY15WA | 3B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 12:30,28/Dec | 58 | 12:30,11/Jul | 18
[14 empty] | 3BGYMTMY15WA | 3B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,21/Feb | 52 | 01:30,14/Jul | 15
[14 empty] | 3BKITCHEN CAFETERIATMY15WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 14:30,28/Feb | 58 | 05:30,06/Sep | 17
[14 empty] | 3BFLOOR 1MIN | 3B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 9 | 06:30,19/Jan | 98 | 15:30,27/Jul | 61
[14 empty] | 3BMECHMIN | 3B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 08:30,19/Oct | 48 | 07:30,17/Jan | 19
[14 empty] | 3BFLOOR 2MIN | 3B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 9 | 06:30,18/Jan | 100 | 16:30,27/Jul | 66
[14 empty] | 3BAUDITORIUMMIN | 3B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 21:30,25/Feb | 56 | 10:30,24/Jul | 15
[14 empty] | 3BGYMMIN | 3B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 10:30,19/Jan | 43 | 05:30,30/Jul | 12
[14 empty] | 3BKITCHEN CAFETERIAMIN | 3B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 08:30,12/Apr | 54 | 06:30,24/Jul | 13
[14 empty] | 3BFLOOR 1MAX | 3B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 45 | 04:30,04/Jan | 100 | 16:30,01/Sep | 84
[14 empty] | 3BMECHMAX | 3B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 03:30,08/Dec | 53 | 15:30,01/Sep | 23
[14 empty] | 3BFLOOR 2MAX | 3B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 45 | 05:30,04/Jan | 100 | 14:30,07/May | 85
[14 empty] | 3BAUDITORIUMMAX | 3B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 23:30,20/Jan | 58 | 14:30,08/Aug | 19
[14 empty] | 3BGYMMAX | 3B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 15:30,10/Jan | 54 | 04:30,10/Sep | 17
[14 empty] | 3BKITCHEN CAFETERIAMAX | 3B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 08:30,13/Dec | 53 | 01:30,27/Jul | 20
[14 empty] | 3CLocationFilename | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 3CFLOOR 1TMY7WA | 3C | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 25 | 04:30,11/Jan | 93 | 15:30,08/Sep | 64
[14 empty] | 3CMECHTMY7WA | 3C | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 03:30,09/May | 28 | 14:30,14/Oct | 8
[14 empty] | 3CFLOOR 2TMY7WA | 3C | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 28 | 07:30,10/Jan | 99 | 14:30,14/Oct | 72
[14 empty] | 3CAUDITORIUMTMY7WA | 3C | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 23:30,11/Jun | 26 | 16:30,06/Sep | 7
[14 empty] | 3CGYMTMY7WA | 3C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 13:30,23/May | 21 | 07:30,10/Jan | 7
[14 empty] | 3CKITCHEN CAFETERIATMY7WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 16:30,18/Dec | 27 | 10:30,04/May | 9
[14 empty] | 3CFLOOR 1TMY3WA | 3C | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 31 | 05:30,09/Feb | 95 | 15:30,24/Sep | 71
[14 empty] | 3CMECHTMY3WA | 3C | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 04:30,15/Apr | 33 | 14:30,05/Oct | 11
[14 empty] | 3CFLOOR 2TMY3WA | 3C | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 30 | 05:30,09/Feb | 99 | 14:30,23/Sep | 77
[14 empty] | 3CAUDITORIUMTMY3WA | 3C | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 07:30,24/Apr | 39 | 15:30,03/Oct | 9
[14 empty] | 3CGYMTMY3WA | 3C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 15:30,12/Dec | 21 | 17:30,10/May | 8
[14 empty] | 3CKITCHEN CAFETERIATMY3WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 08:30,10/Feb | 35 | 06:30,25/Sep | 12
[14 empty] | 3CFLOOR 1TMY3 | 3C | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 27 | 04:30,11/Jan | 94 | 14:30,24/Sep | 66
[14 empty] | 3CMECHTMY3 | 3C | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 03:30,09/May | 28 | 13:30,16/Sep | 9
[14 empty] | 3CFLOOR 2TMY3 | 3C | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 29 | 07:30,26/Dec | 99 | 15:30,15/Sep | 73
[14 empty] | 3CAUDITORIUMTMY3 | 3C | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 09:30,08/May | 27 | 16:30,21/Oct | 8
[14 empty] | 3CGYMTMY3 | 3C | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,18/Dec | 19 | 05:30,11/Jan | 7
[14 empty] | 3CKITCHEN CAFETERIATMY3 | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 10:30,02/Jan | 26 | 10:30,12/May | 10
[14 empty] | 3CFLOOR 1TMY2 | 3C | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 24 | 06:30,26/Dec | 96 | 14:30,30/Sep | 63
[14 empty] | 3CMECHTMY2 | 3C | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 02:30,16/May | 33 | 13:30,29/Sep | 9
[14 empty] | 3CFLOOR 2TMY2 | 3C | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 23 | 05:30,26/Dec | 100 | 15:30,28/Sep | 70
[14 empty] | 3CAUDITORIUMTMY2 | 3C | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 21:30,27/Dec | 43 | 14:30,03/Jul | 8
[14 empty] | 3CGYMTMY2 | 3C | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 15:30,20/Feb | 26 | 04:30,26/Dec | 8
[14 empty] | 3CKITCHEN CAFETERIATMY2 | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 20:30,31/Dec | 35 | 02:30,30/Sep | 9
[14 empty] | 3CFLOOR 1TMY15WA | 3C | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 36 | 07:30,25/Dec | 95 | 14:30,20/Sep | 67
[14 empty] | 3CMECHTMY15WA | 3C | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 05:30,10/Jun | 34 | 13:30,20/Sep | 9
[14 empty] | 3CFLOOR 2TMY15WA | 3C | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 36 | 04:30,25/Jan | 99 | 13:30,17/Sep | 74
[14 empty] | 3CAUDITORIUMTMY15WA | 3C | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 12:30,22/Jan | 50 | 14:30,19/Sep | 8
[14 empty] | 3CGYMTMY15WA | 3C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 10:30,03/Jan | 19 | 17:30,31/May | 8
[14 empty] | 3CKITCHEN CAFETERIATMY15WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 10:30,10/Jan | 35 | 20:30,19/Sep | 11
[14 empty] | 3CFLOOR 1MIN | 3C | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 23 | 04:30,13/Jan | 86 | 15:30,10/Sep | 53
[14 empty] | 3CMECHMIN | 3C | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 03:30,13/Sep | 31 | 04:30,01/Feb | 9
[14 empty] | 3CFLOOR 2MIN | 3C | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 23 | 05:30,13/Jan | 97 | 15:30,10/Sep | 61
[14 empty] | 3CAUDITORIUMMIN | 3C | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 19:30,12/Jan | 26 | 04:30,06/Dec | 9
[14 empty] | 3CGYMMIN | 3C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 09:30,08/May | 29 | 07:30,31/Jan | 8
[14 empty] | 3CKITCHEN CAFETERIAMIN | 3C | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 12:30,20/Feb | 20 | 12:30,10/Sep | 7
[14 empty] | 3CFLOOR 1MAX | 3C | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 48 | 23:30,03/Jan | 96 | 14:30,30/Sep | 76
[14 empty] | 3CMECHMAX | 3C | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 04:30,20/Jan | 37 | 14:30,30/Sep | 14
[14 empty] | 3CFLOOR 2MAX | 3C | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 50 | 23:30,03/Jan | 100 | 15:30,07/May | 81
[14 empty] | 3CAUDITORIUMMAX | 3C | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 04:30,05/Feb | 51 | 14:30,25/Jul | 11
[14 empty] | 3CGYMMAX | 3C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 11:30,03/Jan | 25 | 19:30,29/Aug | 9
[14 empty] | 3CKITCHEN CAFETERIAMAX | 3C | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 08:30,18/Jan | 39 | 19:30,29/Aug | 15
[14 empty] | 4ALocationFilename | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 4AFLOOR 1TMY7WA LPD | 4A | Heating plant sensible load | FLOOR 1 | TMY7WA LPD | Load (Btu/h) | 0 | 04:30,06/Feb | 2780 | 05:30,26/Jul | 247
[14 empty] | 4AMECHTMY7WA LPD | 4A | Heating plant sensible load | MECH | TMY7WA LPD | Load (Btu/h) | 0 | 07:30,01/Jan | 114 | 21:30,18/May | 13
[14 empty] | 4AFLOOR 2TMY7WA LPD | 4A | Heating plant sensible load | FLOOR 2 | TMY7WA LPD | Load (Btu/h) | 0 | 12:30,31/Jan | 3364 | 05:30,15/Sep | 362
[14 empty] | 4AAUDITORIUMTMY7WA LPD | 4A | Heating plant sensible load | AUDITORIUM | TMY7WA LPD | Load (Btu/h) | 0 | 16:30,01/Jan | 161 | 13:30,14/Jan | 21
[14 empty] | 4AGYMTMY7WA LPD | 4A | Heating plant sensible load | GYM | TMY7WA LPD | Load (Btu/h) | 0 | 06:30,27/Jan | 303 | 09:30,29/May | 45
[14 empty] | 4AKITCHEN CAFETERIATMY7WA LPD | 4A | Heating plant sensible load | KITCHEN CAFETERIA | TMY7WA LPD | Load (Btu/h) | 0 | 07:30,22/Jan | 478 | 16:30,22/Jan | 62
[14 empty] | 4AFLOOR 1TMY3WA LPD | 4A | Heating plant sensible load | FLOOR 1 | TMY3WA LPD | Load (Btu/h) | 0 | 10:30,09/Jan | 2780 | 05:30,26/Jul | 247
[14 empty] | 4AMECHTMY3WA LPD | 4A | Heating plant sensible load | MECH | TMY3WA LPD | Load (Btu/h) | 0 | 07:30,01/Jan | 113 | 20:30,08/Jun | 13
[14 empty] | 4AFLOOR 2TMY3WA LPD | 4A | Heating plant sensible load | FLOOR 2 | TMY3WA LPD | Load (Btu/h) | 0 | 10:30,09/Jan | 3457 | 05:30,28/Jun | 364
[14 empty] | 4AAUDITORIUMTMY3WA LPD | 4A | Heating plant sensible load | AUDITORIUM | TMY3WA LPD | Load (Btu/h) | 0 | 22:30,03/Jan | 153 | 21:30,11/Jan | 20
[14 empty] | 4AGYMTMY3WA LPD | 4A | Heating plant sensible load | GYM | TMY3WA LPD | Load (Btu/h) | 0 | 18:30,13/Jan | 290 | 20:30,30/Jun | 44
[14 empty] | 4AKITCHEN CAFETERIATMY3WA LPD | 4A | Heating plant sensible load | KITCHEN CAFETERIA | TMY3WA LPD | Load (Btu/h) | 0 | 08:30,10/Jan | 450 | 06:30,28/Jun | 59
[14 empty] | 4AFLOOR 1TMY3 LPD | 4A | Heating plant sensible load | FLOOR 1 | TMY3 LPD | Load (Btu/h) | 0 | 03:30,02/Feb | 2661 | 17:30,19/Jan | 260
[14 empty] | 4AMECHTMY3 LPD | 4A | Heating plant sensible load | MECH | TMY3 LPD | Load (Btu/h) | 0 | 00:30,01/Jan | 123 | 21:30,26/Mar | 13
[14 empty] | 4AFLOOR 2TMY3 LPD | 4A | Heating plant sensible load | FLOOR 2 | TMY3 LPD | Load (Btu/h) | 0 | 11:30,20/Feb | 3217 | 05:30,02/Aug | 375
[14 empty] | 4AAUDITORIUMTMY3 LPD | 4A | Heating plant sensible load | AUDITORIUM | TMY3 LPD | Load (Btu/h) | 0 | 04:30,01/Jan | 175 | 22:30,19/Jan | 22
[14 empty] | 4AGYMTMY3 LPD | 4A | Heating plant sensible load | GYM | TMY3 LPD | Load (Btu/h) | 0 | 09:30,01/Feb | 303 | 22:30,18/Jan | 46
[14 empty] | 4AKITCHEN CAFETERIATMY3 LPD | 4A | Heating plant sensible load | KITCHEN CAFETERIA | TMY3 LPD | Load (Btu/h) | 0 | 08:30,10/Jan | 488 | 08:30,11/Jul | 66
[14 empty] | 4AFLOOR 1TMY2 LPD | 4A | Heating plant sensible load | FLOOR 1 | TMY2 LPD | Load (Btu/h) | 0 | 09:30,09/Jan | 2799 | 17:30,18/Jan | 263
[14 empty] | 4AMECHTMY2 LPD | 4A | Heating plant sensible load | MECH | TMY2 LPD | Load (Btu/h) | 0 | 02:30,01/Jan | 124 | 21:30,22/Apr | 13
[14 empty] | 4AFLOOR 2TMY2 LPD | 4A | Heating plant sensible load | FLOOR 2 | TMY2 LPD | Load (Btu/h) | 0 | 09:30,09/Jan | 3326 | 05:30,26/Jul | 377
[14 empty] | 4AAUDITORIUMTMY2 LPD | 4A | Heating plant sensible load | AUDITORIUM | TMY2 LPD | Load (Btu/h) | 0 | 07:30,01/Jan | 193 | 20:30,14/Jan | 23
[14 empty] | 4AGYMTMY2 LPD | 4A | Heating plant sensible load | GYM | TMY2 LPD | Load (Btu/h) | 0 | 13:30,05/Jan | 296 | 22:30,18/Jan | 47
[14 empty] | 4AKITCHEN CAFETERIATMY2 LPD | 4A | Heating plant sensible load | KITCHEN CAFETERIA | TMY2 LPD | Load (Btu/h) | 0 | 07:30,05/Jan | 444 | 16:30,21/Dec | 68
[14 empty] | 4AFLOOR 1MIN LPD | 4A | Heating plant sensible load | FLOOR 1 | MIN LPD | Load (Btu/h) | 0 | 14:30,17/Apr | 2829 | 17:30,01/Feb | 296
[14 empty] | 4AMECHMIN LPD | 4A | Heating plant sensible load | MECH | MIN LPD | Load (Btu/h) | 0 | 07:30,01/Jan | 145 | 21:30,10/May | 12
[14 empty] | 4AFLOOR 2MIN LPD | 4A | Heating plant sensible load | FLOOR 2 | MIN LPD | Load (Btu/h) | 0 | 15:30,14/Mar | 3123 | 17:30,05/Feb | 399
[14 empty] | 4AAUDITORIUMMIN LPD | 4A | Heating plant sensible load | AUDITORIUM | MIN LPD | Load (Btu/h) | 0 | 07:30,01/Jan | 182 | 21:30,15/Dec | 32
[14 empty] | 4AGYMMIN LPD | 4A | Heating plant sensible load | GYM | MIN LPD | Load (Btu/h) | 0 | 09:30,23/Jan | 327 | 22:30,25/Jan | 54
[14 empty] | 4AKITCHEN CAFETERIAMIN LPD | 4A | Heating plant sensible load | KITCHEN CAFETERIA | MIN LPD | Load (Btu/h) | 0 | 08:30,21/Feb | 491 | 16:30,30/Dec | 91
[14 empty] | 4AFLOOR 1TMY15WA LPD | 4A | Heating plant sensible load | FLOOR 1 | TMY15WA LPD | Load (Btu/h) | 0 | 03:30,01/Jan | 2780 | 05:30,26/Jul | 248
[14 empty] | 4AMECHTMY15WA LPD | 4A | Heating plant sensible load | MECH | TMY15WA LPD | Load (Btu/h) | 0 | 03:30,01/Jan | 114 | 21:30,18/May | 13
[14 empty] | 4AFLOOR 2TMY15WA LPD | 4A | Heating plant sensible load | FLOOR 2 | TMY15WA LPD | Load (Btu/h) | 0 | 13:30,02/Jan | 3457 | 05:30,28/Jun | 367
[14 empty] | 4AAUDITORIUMTMY15WA LPD | 4A | Heating plant sensible load | AUDITORIUM | TMY15WA LPD | Load (Btu/h) | 0 | 04:30,01/Jan | 168 | 21:30,01/Feb | 20
[14 empty] | 4AGYMTMY15WA LPD | 4A | Heating plant sensible load | GYM | TMY15WA LPD | Load (Btu/h) | 0 | 07:30,06/Jan | 313 | 09:30,11/Sep | 44
[14 empty] | 4AKITCHEN CAFETERIATMY15WA LPD | 4A | Heating plant sensible load | KITCHEN CAFETERIA | TMY15WA LPD | Load (Btu/h) | 0 | 03:30,01/Jan | 450 | 06:30,28/Jun | 60
[14 empty] | 4AFLOOR 1MAX LPD | 4A | Heating plant sensible load | FLOOR 1 | MAX LPD | Load (Btu/h) | 0 | 10:30,02/Jan | 3135 | 05:30,02/Aug | 244
[14 empty] | 4AMECHMAX LPD | 4A | Heating plant sensible load | MECH | MAX LPD | Load (Btu/h) | 0 | 07:30,01/Jan | 127 | 21:30,27/May | 12
[14 empty] | 4AFLOOR 2MAX LPD | 4A | Heating plant sensible load | FLOOR 2 | MAX LPD | Load (Btu/h) | 0 | 12:30,02/Jan | 3678 | 05:30,02/Aug | 365
[14 empty] | 4AAUDITORIUMMAX LPD | 4A | Heating plant sensible load | AUDITORIUM | MAX LPD | Load (Btu/h) | 0 | 08:30,01/Jan | 157 | 07:30,16/Aug | 16
[14 empty] | 4AGYMMAX LPD | 4A | Heating plant sensible load | GYM | MAX LPD | Load (Btu/h) | 0 | 09:30,03/Jan | 332 | 08:30,01/Jun | 40
[14 empty] | 4AKITCHEN CAFETERIAMAX LPD | 4A | Heating plant sensible load | KITCHEN CAFETERIA | MAX LPD | Load (Btu/h) | 0 | 22:30,02/Jan | 446 | 06:30,26/Jul | 49
[14 empty] | 4BLocationFilename | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 4BFLOOR 1TMY7WA LPD | 4B | People dissatisfied | FLOOR 1 | TMY7WA LPD | Percentage (%) | 5 | 06:30,17/May | 41 | 15:30,18/Jul | 13
[14 empty] | 4BMECHTMY7WA LPD | 4B | People dissatisfied | MECH | TMY7WA LPD | Percentage (%) | 5 | 22:30,11/Oct | 71 | 14:30,20/Jul | 20
[14 empty] | 4BFLOOR 2TMY7WA LPD | 4B | People dissatisfied | FLOOR 2 | TMY7WA LPD | Percentage (%) | 5 | 07:30,22/Oct | 51 | 12:30,18/Jul | 15
[14 empty] | 4BAUDITORIUMTMY7WA LPD | 4B | People dissatisfied | AUDITORIUM | TMY7WA LPD | Percentage (%) | 5 | 17:30,25/Nov | 54 | 13:30,18/Jul | 15
[14 empty] | 4BGYMTMY7WA LPD | 4B | People dissatisfied | GYM | TMY7WA LPD | Percentage (%) | 5 | 10:30,03/Feb | 61 | 18:30,02/Sep | 14
[14 empty] | 4BKITCHEN CAFETERIATMY7WA LPD | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA LPD | Percentage (%) | 5 | 18:30,25/Jan | 41 | 18:30,18/Jul | 12
[14 empty] | 4BFLOOR 1TMY3WA LPD | 4B | People dissatisfied | FLOOR 1 | TMY3WA LPD | Percentage (%) | 5 | 06:30,04/May | 41 | 14:30,01/Aug | 13
[14 empty] | 4BMECHTMY3WA LPD | 4B | People dissatisfied | MECH | TMY3WA LPD | Percentage (%) | 5 | 08:30,05/Nov | 67 | 14:30,06/Jul | 21
[14 empty] | 4BFLOOR 2TMY3WA LPD | 4B | People dissatisfied | FLOOR 2 | TMY3WA LPD | Percentage (%) | 5 | 06:30,12/May | 54 | 12:30,11/Jul | 15
[14 empty] | 4BAUDITORIUMTMY3WA LPD | 4B | People dissatisfied | AUDITORIUM | TMY3WA LPD | Percentage (%) | 5 | 13:30,28/Jan | 55 | 13:30,11/Jul | 14
[14 empty] | 4BGYMTMY3WA LPD | 4B | People dissatisfied | GYM | TMY3WA LPD | Percentage (%) | 5 | 21:30,02/Nov | 62 | 18:30,02/Sep | 16
[14 empty] | 4BKITCHEN CAFETERIATMY3WA LPD | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA LPD | Percentage (%) | 5 | 16:30,25/Nov | 38 | 07:30,01/Aug | 12
[14 empty] | 4BFLOOR 1TMY3 LPD | 4B | People dissatisfied | FLOOR 1 | TMY3 LPD | Percentage (%) | 5 | 06:30,27/Apr | 44 | 14:30,25/Jul | 14
[14 empty] | 4BMECHTMY3 LPD | 4B | People dissatisfied | MECH | TMY3 LPD | Percentage (%) | 5 | 00:30,18/Apr | 65 | 14:30,29/Jun | 21
[14 empty] | 4BFLOOR 2TMY3 LPD | 4B | People dissatisfied | FLOOR 2 | TMY3 LPD | Percentage (%) | 5 | 07:30,11/May | 51 | 13:30,25/Jul | 16
[14 empty] | 4BAUDITORIUMTMY3 LPD | 4B | People dissatisfied | AUDITORIUM | TMY3 LPD | Percentage (%) | 5 | 09:30,18/Oct | 54 | 12:30,15/Aug | 15
[14 empty] | 4BGYMTMY3 LPD | 4B | People dissatisfied | GYM | TMY3 LPD | Percentage (%) | 5 | 12:30,22/Feb | 63 | 18:30,20/May | 15
[14 empty] | 4BKITCHEN CAFETERIATMY3 LPD | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY3 LPD | Percentage (%) | 5 | 16:30,09/Feb | 42 | 07:30,04/Jul | 13
[14 empty] | 4BFLOOR 1TMY2 LPD | 4B | People dissatisfied | FLOOR 1 | TMY2 LPD | Percentage (%) | 5 | 07:30,10/May | 46 | 17:30,01/Aug | 14
[14 empty] | 4BMECHTMY2 LPD | 4B | People dissatisfied | MECH | TMY2 LPD | Percentage (%) | 5 | 23:30,08/May | 62 | 16:30,01/Aug | 20
[14 empty] | 4BFLOOR 2TMY2 LPD | 4B | People dissatisfied | FLOOR 2 | TMY2 LPD | Percentage (%) | 5 | 07:30,13/Oct | 53 | 14:30,01/Aug | 16
[14 empty] | 4BAUDITORIUMTMY2 LPD | 4B | People dissatisfied | AUDITORIUM | TMY2 LPD | Percentage (%) | 5 | 20:30,04/Feb | 54 | 15:30,01/Aug | 15
[14 empty] | 4BGYMTMY2 LPD | 4B | People dissatisfied | GYM | TMY2 LPD | Percentage (%) | 5 | 16:30,03/Feb | 63 | 18:30,31/May | 15
[14 empty] | 4BKITCHEN CAFETERIATMY2 LPD | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY2 LPD | Percentage (%) | 5 | 19:30,12/Feb | 50 | 18:30,01/Aug | 13
[14 empty] | 4BFLOOR 1MIN LPD | 4B | People dissatisfied | FLOOR 1 | MIN LPD | Percentage (%) | 5 | 07:30,16/Jun | 41 | 04:30,03/Feb | 15
[14 empty] | 4BMECHMIN LPD | 4B | People dissatisfied | MECH | MIN LPD | Percentage (%) | 5 | 09:30,13/Jun | 70 | 06:30,03/Feb | 20
[14 empty] | 4BFLOOR 2MIN LPD | 4B | People dissatisfied | FLOOR 2 | MIN LPD | Percentage (%) | 5 | 07:30,04/Jun | 46 | 15:30,01/Aug | 16
[14 empty] | 4BAUDITORIUMMIN LPD | 4B | People dissatisfied | AUDITORIUM | MIN LPD | Percentage (%) | 5 | 01:30,09/Jun | 46 | 04:30,03/Feb | 16
[14 empty] | 4BGYMMIN LPD | 4B | People dissatisfied | GYM | MIN LPD | Percentage (%) | 5 | 11:30,27/Jan | 56 | 19:30,31/May | 12
[14 empty] | 4BKITCHEN CAFETERIAMIN LPD | 4B | People dissatisfied | KITCHEN CAFETERIA | MIN LPD | Percentage (%) | 5 | 15:30,26/Nov | 39 | 03:30,27/Dec | 12
[14 empty] | 4BFLOOR 1TMY15WA LPD | 4B | People dissatisfied | FLOOR 1 | TMY15WA LPD | Percentage (%) | 5 | 06:30,27/Apr | 41 | 15:30,18/Jul | 13
[14 empty] | 4BMECHTMY15WA LPD | 4B | People dissatisfied | MECH | TMY15WA LPD | Percentage (%) | 5 | 21:30,05/Nov | 71 | 14:30,20/Jul | 20
[14 empty] | 4BFLOOR 2TMY15WA LPD | 4B | People dissatisfied | FLOOR 2 | TMY15WA LPD | Percentage (%) | 5 | 06:30,22/Apr | 52 | 15:30,21/Aug | 16
[14 empty] | 4BAUDITORIUMTMY15WA LPD | 4B | People dissatisfied | AUDITORIUM | TMY15WA LPD | Percentage (%) | 5 | 07:30,02/May | 54 | 13:30,18/Jul | 15
[14 empty] | 4BGYMTMY15WA LPD | 4B | People dissatisfied | GYM | TMY15WA LPD | Percentage (%) | 5 | 10:30,21/Dec | 60 | 18:30,24/Sep | 15
[14 empty] | 4BKITCHEN CAFETERIATMY15WA LPD | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA LPD | Percentage (%) | 5 | 18:30,25/Jan | 41 | 18:30,18/Jul | 12
[14 empty] | 4BFLOOR 1MAX LPD | 4B | People dissatisfied | FLOOR 1 | MAX LPD | Percentage (%) | 5 | 07:30,07/Apr | 43 | 16:30,18/Jul | 14
[14 empty] | 4BMECHMAX LPD | 4B | People dissatisfied | MECH | MAX LPD | Percentage (%) | 5 | 23:30,21/Mar | 74 | 14:30,20/Jul | 24
[14 empty] | 4BFLOOR 2MAX LPD | 4B | People dissatisfied | FLOOR 2 | MAX LPD | Percentage (%) | 5 | 07:30,23/Apr | 52 | 13:30,28/Aug | 16
[14 empty] | 4BAUDITORIUMMAX LPD | 4B | People dissatisfied | AUDITORIUM | MAX LPD | Percentage (%) | 5 | 15:30,06/Jan | 53 | 15:30,18/Jul | 15
[14 empty] | 4BGYMMAX LPD | 4B | People dissatisfied | GYM | MAX LPD | Percentage (%) | 5 | 09:30,03/Feb | 68 | 18:30,31/May | 19
[14 empty] | 4BKITCHEN CAFETERIAMAX LPD | 4B | People dissatisfied | KITCHEN CAFETERIA | MAX LPD | Percentage (%) | 5 | 18:30,04/Jan | 42 | 18:30,25/Jul | 13
[14 empty] | 4CLocationFilename | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 4CFLOOR 1TMY7WA LPD | 4C | People dissatisfied | FLOOR 1 | TMY7WA LPD | Percentage (%) | 5 | 06:30,10/Jun | 40 | 15:30,01/Aug | 11
[14 empty] | 4CMECHTMY7WA LPD | 4C | People dissatisfied | MECH | TMY7WA LPD | Percentage (%) | 5 | 08:30,18/Jun | 55 | 14:30,29/Jul | 14
[14 empty] | 4CFLOOR 2TMY7WA LPD | 4C | People dissatisfied | FLOOR 2 | TMY7WA LPD | Percentage (%) | 5 | 07:30,14/Oct | 53 | 15:30,01/Aug | 13
[14 empty] | 4CAUDITORIUMTMY7WA LPD | 4C | People dissatisfied | AUDITORIUM | TMY7WA LPD | Percentage (%) | 5 | 03:30,07/May | 53 | 13:30,01/Aug | 12
[14 empty] | 4CGYMTMY7WA LPD | 4C | People dissatisfied | GYM | TMY7WA LPD | Percentage (%) | 5 | 14:30,17/Apr | 48 | 17:30,07/May | 10
[14 empty] | 4CKITCHEN CAFETERIATMY7WA LPD | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA LPD | Percentage (%) | 5 | 18:30,25/Feb | 36 | 19:30,01/Aug | 9
[14 empty] | 4CFLOOR 1TMY3WA LPD | 4C | People dissatisfied | FLOOR 1 | TMY3WA LPD | Percentage (%) | 5 | 23:30,16/Jun | 31 | 16:30,14/Aug | 10
[14 empty] | 4CMECHTMY3WA LPD | 4C | People dissatisfied | MECH | TMY3WA LPD | Percentage (%) | 5 | 22:30,28/Aug | 45 | 16:30,15/Sep | 12
[14 empty] | 4CFLOOR 2TMY3WA LPD | 4C | People dissatisfied | FLOOR 2 | TMY3WA LPD | Percentage (%) | 5 | 06:30,13/Sep | 48 | 15:30,11/Jul | 12
[14 empty] | 4CAUDITORIUMTMY3WA LPD | 4C | People dissatisfied | AUDITORIUM | TMY3WA LPD | Percentage (%) | 5 | 09:30,11/Mar | 41 | 16:30,14/Aug | 11
[14 empty] | 4CGYMTMY3WA LPD | 4C | People dissatisfied | GYM | TMY3WA LPD | Percentage (%) | 5 | 14:30,13/Feb | 50 | 17:30,06/Sep | 9
[14 empty] | 4CKITCHEN CAFETERIATMY3WA LPD | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA LPD | Percentage (%) | 5 | 19:30,27/Dec | 28 | 18:30,15/Aug | 9
[14 empty] | 4CFLOOR 1TMY3 LPD | 4C | People dissatisfied | FLOOR 1 | TMY3 LPD | Percentage (%) | 5 | 07:30,06/Oct | 33 | 19:30,10/Aug | 11
[14 empty] | 4CMECHTMY3 LPD | 4C | People dissatisfied | MECH | TMY3 LPD | Percentage (%) | 5 | 23:30,20/Oct | 41 | 18:30,21/Jul | 13
[14 empty] | 4CFLOOR 2TMY3 LPD | 4C | People dissatisfied | FLOOR 2 | TMY3 LPD | Percentage (%) | 5 | 07:30,06/Oct | 50 | 18:30,21/Jul | 13
[14 empty] | 4CAUDITORIUMTMY3 LPD | 4C | People dissatisfied | AUDITORIUM | TMY3 LPD | Percentage (%) | 5 | 08:30,16/Nov | 40 | 16:30,05/Jun | 11
[14 empty] | 4CGYMTMY3 LPD | 4C | People dissatisfied | GYM | TMY3 LPD | Percentage (%) | 5 | 08:30,25/Mar | 47 | 19:30,05/Apr | 9
[14 empty] | 4CKITCHEN CAFETERIATMY3 LPD | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY3 LPD | Percentage (%) | 5 | 18:30,13/Jan | 33 | 19:30,08/Aug | 10
[14 empty] | 4CFLOOR 1TMY2 LPD | 4C | People dissatisfied | FLOOR 1 | TMY2 LPD | Percentage (%) | 5 | 07:30,09/Apr | 32 | 03:30,31/Jan | 11
[14 empty] | 4CMECHTMY2 LPD | 4C | People dissatisfied | MECH | TMY2 LPD | Percentage (%) | 5 | 20:30,10/Oct | 37 | 16:30,10/Sep | 13
[14 empty] | 4CFLOOR 2TMY2 LPD | 4C | People dissatisfied | FLOOR 2 | TMY2 LPD | Percentage (%) | 5 | 07:30,04/Oct | 46 | 17:30,15/Aug | 13
[14 empty] | 4CAUDITORIUMTMY2 LPD | 4C | People dissatisfied | AUDITORIUM | TMY2 LPD | Percentage (%) | 5 | 10:30,31/Mar | 42 | 08:30,31/Jan | 11
[14 empty] | 4CGYMTMY2 LPD | 4C | People dissatisfied | GYM | TMY2 LPD | Percentage (%) | 5 | 14:30,31/Oct | 54 | 18:30,17/May | 9
[14 empty] | 4CKITCHEN CAFETERIATMY2 LPD | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY2 LPD | Percentage (%) | 5 | 13:30,07/Nov | 33 | 19:30,15/Aug | 10
[14 empty] | 4CFLOOR 1MIN LPD | 4C | People dissatisfied | FLOOR 1 | MIN LPD | Percentage (%) | 5 | 07:30,02/Jul | 35 | 07:30,07/Feb | 14
[14 empty] | 4CMECHMIN LPD | 4C | People dissatisfied | MECH | MIN LPD | Percentage (%) | 5 | 09:30,28/Jul | 45 | 06:30,08/Dec | 18
[14 empty] | 4CFLOOR 2MIN LPD | 4C | People dissatisfied | FLOOR 2 | MIN LPD | Percentage (%) | 5 | 09:30,10/Jun | 36 | 04:30,08/Dec | 15
[14 empty] | 4CAUDITORIUMMIN LPD | 4C | People dissatisfied | AUDITORIUM | MIN LPD | Percentage (%) | 5 | 15:30,22/Mar | 44 | 17:30,05/Dec | 15
[14 empty] | 4CGYMMIN LPD | 4C | People dissatisfied | GYM | MIN LPD | Percentage (%) | 5 | 13:30,25/Feb | 37 | 06:30,07/Feb | 10
[14 empty] | 4CKITCHEN CAFETERIAMIN LPD | 4C | People dissatisfied | KITCHEN CAFETERIA | MIN LPD | Percentage (%) | 5 | 16:30,10/Mar | 37 | 07:30,07/Feb | 10
[14 empty] | 4CFLOOR 1TMY15WA LPD | 4C | People dissatisfied | FLOOR 1 | TMY15WA LPD | Percentage (%) | 5 | 06:30,10/Jun | 40 | 15:30,01/Aug | 11
[14 empty] | 4CMECHTMY15WA LPD | 4C | People dissatisfied | MECH | TMY15WA LPD | Percentage (%) | 5 | 22:30,28/Oct | 55 | 14:30,29/Jul | 13
[14 empty] | 4CFLOOR 2TMY15WA LPD | 4C | People dissatisfied | FLOOR 2 | TMY15WA LPD | Percentage (%) | 5 | 07:30,22/Apr | 53 | 15:30,01/Aug | 13
[14 empty] | 4CAUDITORIUMTMY15WA LPD | 4C | People dissatisfied | AUDITORIUM | TMY15WA LPD | Percentage (%) | 5 | 12:30,26/Mar | 53 | 13:30,01/Aug | 12
[14 empty] | 4CGYMTMY15WA LPD | 4C | People dissatisfied | GYM | TMY15WA LPD | Percentage (%) | 5 | 08:30,09/Dec | 45 | 17:30,06/Sep | 9
[14 empty] | 4CKITCHEN CAFETERIATMY15WA LPD | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA LPD | Percentage (%) | 5 | 15:30,13/Mar | 36 | 19:30,01/Aug | 9
[14 empty] | 4CFLOOR 1MAX LPD | 4C | People dissatisfied | FLOOR 1 | MAX LPD | Percentage (%) | 5 | 07:30,16/Apr | 43 | 17:30,15/Aug | 12
[14 empty] | 4CMECHMAX LPD | 4C | People dissatisfied | MECH | MAX LPD | Percentage (%) | 5 | 09:30,02/Nov | 59 | 15:30,29/Jul | 15
[14 empty] | 4CFLOOR 2MAX LPD | 4C | People dissatisfied | FLOOR 2 | MAX LPD | Percentage (%) | 5 | 07:30,25/Mar | 55 | 16:30,11/Sep | 14
[14 empty] | 4CAUDITORIUMMAX LPD | 4C | People dissatisfied | AUDITORIUM | MAX LPD | Percentage (%) | 5 | 22:30,19/Apr | 55 | 15:30,31/Jul | 12
[14 empty] | 4CGYMMAX LPD | 4C | People dissatisfied | GYM | MAX LPD | Percentage (%) | 5 | 10:30,14/Mar | 58 | 17:30,06/Sep | 12
[14 empty] | 4CKITCHEN CAFETERIAMAX LPD | 4C | People dissatisfied | KITCHEN CAFETERIA | MAX LPD | Percentage (%) | 5 | 08:30,14/Apr | 46 | 19:30,15/Aug | 12
[14 empty] | 5ALocationFilename | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 5AFLOOR 15A_TMY7_WA | 5A | People dissatisfied | FLOOR 1 | 5A_TMY7_WA | Percentage (%) | 5 | 07:30,21/Oct | 49 | 11:30,25/Jul | 15
[14 empty] | 5AMECH5A_TMY7_WA | 5A | People dissatisfied | MECH | 5A_TMY7_WA | Percentage (%) | 5 | 08:30,11/May | 69 | 16:30,09/Sep | 21
[14 empty] | 5AFLOOR 25A_TMY7_WA | 5A | People dissatisfied | FLOOR 2 | 5A_TMY7_WA | Percentage (%) | 5 | 07:30,27/Oct | 56 | 13:30,01/Aug | 17
[14 empty] | 5AAUDITORIUM5A_TMY7_WA | 5A | People dissatisfied | AUDITORIUM | 5A_TMY7_WA | Percentage (%) | 5 | 07:30,07/Oct | 63 | 11:30,24/Jul | 16
[14 empty] | 5AGYM5A_TMY7_WA | 5A | People dissatisfied | GYM | 5A_TMY7_WA | Percentage (%) | 5 | 08:30,09/Apr | 39 | 07:30,24/Jan | 11
[14 empty] | 5AKITCHEN CAFETERIA5A_TMY7_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY7_WA | Percentage (%) | 5 | 17:30,31/Dec | 52 | 01:30,19/Jul | 14
[14 empty] | 5AFLOOR 15A_TMY3_WA | 5A | People dissatisfied | FLOOR 1 | 5A_TMY3_WA | Percentage (%) | 5 | 07:30,19/Nov | 51 | 18:30,15/Aug | 15
[14 empty] | 5AMECH5A_TMY3_WA | 5A | People dissatisfied | MECH | 5A_TMY3_WA | Percentage (%) | 5 | 08:30,16/Nov | 69 | 16:30,13/Sep | 21
[14 empty] | 5AFLOOR 25A_TMY3_WA | 5A | People dissatisfied | FLOOR 2 | 5A_TMY3_WA | Percentage (%) | 5 | 07:30,19/Nov | 55 | 16:30,18/Jul | 17
[14 empty] | 5AAUDITORIUM5A_TMY3_WA | 5A | People dissatisfied | AUDITORIUM | 5A_TMY3_WA | Percentage (%) | 5 | 08:30,25/Nov | 61 | 12:30,29/Aug | 16
[14 empty] | 5AGYM5A_TMY3_WA | 5A | People dissatisfied | GYM | 5A_TMY3_WA | Percentage (%) | 5 | 13:30,09/May | 44 | 18:30,23/Sep | 11
[14 empty] | 5AKITCHEN CAFETERIA5A_TMY3_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY3_WA | Percentage (%) | 5 | 16:30,05/Mar | 51 | 23:30,14/Aug | 14
[14 empty] | 5AFLOOR 15A_TMY3 | 5A | People dissatisfied | FLOOR 1 | 5A_TMY3 | Percentage (%) | 5 | 15:30,10/Nov | 53 | 01:30,19/Jul | 15
[14 empty] | 5AMECH5A_TMY3 | 5A | People dissatisfied | MECH | 5A_TMY3 | Percentage (%) | 5 | 01:30,04/May | 69 | 14:30,19/Jul | 21
[14 empty] | 5AFLOOR 25A_TMY3 | 5A | People dissatisfied | FLOOR 2 | 5A_TMY3 | Percentage (%) | 5 | 06:30,20/Apr | 57 | 15:30,18/Jul | 17
[14 empty] | 5AAUDITORIUM5A_TMY3 | 5A | People dissatisfied | AUDITORIUM | 5A_TMY3 | Percentage (%) | 5 | 23:30,05/Oct | 63 | 11:30,17/Jul | 16
[14 empty] | 5AGYM5A_TMY3 | 5A | People dissatisfied | GYM | 5A_TMY3 | Percentage (%) | 5 | 12:30,23/Oct | 47 | 05:30,07/Feb | 11
[14 empty] | 5AKITCHEN CAFETERIA5A_TMY3 | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY3 | Percentage (%) | 5 | 18:30,18/Mar | 59 | 20:30,18/Jul | 14
[14 empty] | 5AFLOOR 15A_TMY2 | 5A | People dissatisfied | FLOOR 1 | 5A_TMY2 | Percentage (%) | 5 | 07:30,01/Oct | 47 | 18:30,18/Jul | 15
[14 empty] | 5AMECH5A_TMY2 | 5A | People dissatisfied | MECH | 5A_TMY2 | Percentage (%) | 5 | 01:30,04/May | 60 | 14:30,19/Jul | 20
[14 empty] | 5AFLOOR 25A_TMY2 | 5A | People dissatisfied | FLOOR 2 | 5A_TMY2 | Percentage (%) | 5 | 07:30,28/Oct | 53 | 19:30,18/Jul | 17
[14 empty] | 5AAUDITORIUM5A_TMY2 | 5A | People dissatisfied | AUDITORIUM | 5A_TMY2 | Percentage (%) | 5 | 18:30,24/Mar | 59 | 13:30,03/Jul | 16
[14 empty] | 5AGYM5A_TMY2 | 5A | People dissatisfied | GYM | 5A_TMY2 | Percentage (%) | 5 | 11:30,08/Mar | 44 | 18:30,26/May | 11
[14 empty] | 5AKITCHEN CAFETERIA5A_TMY2 | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY2 | Percentage (%) | 5 | 17:30,10/Nov | 50 | 19:30,18/Jul | 14
[14 empty] | 5AFLOOR 15A_TMY15_WA | 5A | People dissatisfied | FLOOR 1 | 5A_TMY15_WA | Percentage (%) | 5 | 07:30,19/Nov | 49 | 11:30,25/Jul | 15
[14 empty] | 5AMECH5A_TMY15_WA | 5A | People dissatisfied | MECH | 5A_TMY15_WA | Percentage (%) | 5 | 08:30,16/Nov | 69 | 16:30,13/Sep | 22
[14 empty] | 5AFLOOR 25A_TMY15_WA | 5A | People dissatisfied | FLOOR 2 | 5A_TMY15_WA | Percentage (%) | 5 | 07:30,30/Sep | 56 | 13:30,01/Aug | 17
[14 empty] | 5AAUDITORIUM5A_TMY15_WA | 5A | People dissatisfied | AUDITORIUM | 5A_TMY15_WA | Percentage (%) | 5 | 08:30,25/Nov | 63 | 11:30,24/Jul | 16
[14 empty] | 5AGYM5A_TMY15_WA | 5A | People dissatisfied | GYM | 5A_TMY15_WA | Percentage (%) | 5 | 14:30,03/Apr | 44 | 18:30,23/Sep | 11
[14 empty] | 5AKITCHEN CAFETERIA5A_TMY15_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_TMY15_WA | Percentage (%) | 5 | 12:30,06/Nov | 52 | 01:30,19/Jul | 14
[14 empty] | 5AFLOOR 15A_MIN_WA | 5A | People dissatisfied | FLOOR 1 | 5A_MIN_WA | Percentage (%) | 5 | 07:30,16/Sep | 42 | 04:30,31/Jan | 16
[14 empty] | 5AMECH5A_MIN_WA | 5A | People dissatisfied | MECH | 5A_MIN_WA | Percentage (%) | 5 | 20:30,18/Sep | 43 | 07:30,31/Jan | 19
[14 empty] | 5AFLOOR 25A_MIN_WA | 5A | People dissatisfied | FLOOR 2 | 5A_MIN_WA | Percentage (%) | 5 | 07:30,16/Sep | 41 | 05:30,31/Jan | 16
[14 empty] | 5AAUDITORIUM5A_MIN_WA | 5A | People dissatisfied | AUDITORIUM | 5A_MIN_WA | Percentage (%) | 5 | 21:30,02/Jun | 46 | 03:30,31/Jan | 16
[14 empty] | 5AGYM5A_MIN_WA | 5A | People dissatisfied | GYM | 5A_MIN_WA | Percentage (%) | 5 | 21:30,01/Nov | 47 | 00:30,31/Jan | 11
[14 empty] | 5AKITCHEN CAFETERIA5A_MIN_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_MIN_WA | Percentage (%) | 5 | 18:30,02/Apr | 40 | 01:30,18/Jan | 12
[14 empty] | 5AFLOOR 15A_MAX_WA | 5A | People dissatisfied | FLOOR 1 | 5A_MAX_WA | Percentage (%) | 5 | 07:30,12/Nov | 58 | 02:30,19/Jul | 17
[14 empty] | 5AMECH5A_MAX_WA | 5A | People dissatisfied | MECH | 5A_MAX_WA | Percentage (%) | 5 | 09:30,11/Mar | 79 | 17:30,02/Sep | 26
[14 empty] | 5AFLOOR 25A_MAX_WA | 5A | People dissatisfied | FLOOR 2 | 5A_MAX_WA | Percentage (%) | 5 | 07:30,28/Apr | 58 | 14:30,07/Aug | 19
[14 empty] | 5AAUDITORIUM5A_MAX_WA | 5A | People dissatisfied | AUDITORIUM | 5A_MAX_WA | Percentage (%) | 5 | 12:30,04/Feb | 62 | 13:30,22/Aug | 17
[14 empty] | 5AGYM5A_MAX_WA | 5A | People dissatisfied | GYM | 5A_MAX_WA | Percentage (%) | 5 | 08:30,11/Feb | 48 | 01:30,26/Jul | 12
[14 empty] | 5AKITCHEN CAFETERIA5A_MAX_WA | 5A | People dissatisfied | KITCHEN CAFETERIA | 5A_MAX_WA | Percentage (%) | 5 | 17:30,15/Jan | 59 | 03:30,19/Jul | 17
[14 empty] | 5BLocationFilename | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 5BFLOOR 1TMY7WA | 5B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,21/Jun | 41 | 01:30,07/Feb | 14
[14 empty] | 5BMECHTMY7WA | 5B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,19/Jul | 17
[14 empty] | 5BFLOOR 2TMY7WA | 5B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 06:30,11/Aug | 50 | 14:30,18/Jul | 15
[14 empty] | 5BAUDITORIUMTMY7WA | 5B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 16:30,25/Jan | 51 | 15:30,18/Jul | 15
[14 empty] | 5BGYMTMY7WA | 5B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 12:30,04/Mar | 52 | 17:30,03/Sep | 12
[14 empty] | 5BKITCHEN CAFETERIATMY7WA | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 11:30,10/Apr | 39 | 07:30,07/Feb | 11
[14 empty] | 5BFLOOR 1TMY3WA | 5B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 06:30,07/Jun | 38 | 04:30,24/Dec | 13
[14 empty] | 5BMECHTMY3WA | 5B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,19/Jul | 17
[14 empty] | 5BFLOOR 2TMY3WA | 5B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 06:30,11/Aug | 50 | 14:30,18/Jul | 15
[14 empty] | 5BAUDITORIUMTMY3WA | 5B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 18:30,08/Jan | 51 | 15:30,18/Jul | 14
[14 empty] | 5BGYMTMY3WA | 5B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 12:30,13/Jan | 52 | 17:30,03/Sep | 12
[14 empty] | 5BKITCHEN CAFETERIATMY3WA | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 12:30,21/Mar | 35 | 05:30,23/Dec | 11
[14 empty] | 5BFLOOR 1TMY3 | 5B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 22:30,10/Jun | 42 | 04:30,13/Dec | 14
[14 empty] | 5BMECHTMY3 | 5B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 23:30,05/Oct | 69 | 16:30,09/Sep | 19
[14 empty] | 5BFLOOR 2TMY3 | 5B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,14/Sep | 47 | 13:30,01/Aug | 15
[14 empty] | 5BAUDITORIUMTMY3 | 5B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 00:30,11/May | 49 | 16:30,27/Jun | 14
[14 empty] | 5BGYMTMY3 | 5B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 10:30,13/Nov | 63 | 19:30,28/May | 14
[14 empty] | 5BKITCHEN CAFETERIATMY3 | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 17:30,27/Jan | 39 | 21:30,17/Jan | 12
[14 empty] | 5BFLOOR 1TMY2 | 5B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,08/Jun | 42 | 04:30,13/Dec | 14
[14 empty] | 5BMECHTMY2 | 5B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 01:30,10/Jun | 70 | 17:30,02/Sep | 19
[14 empty] | 5BFLOOR 2TMY2 | 5B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,04/Oct | 48 | 14:30,04/Jul | 15
[14 empty] | 5BAUDITORIUMTMY2 | 5B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 22:30,29/May | 50 | 16:30,04/Jul | 15
[14 empty] | 5BGYMTMY2 | 5B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 11:30,01/Mar | 65 | 18:30,02/Sep | 13
[14 empty] | 5BKITCHEN CAFETERIATMY2 | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 15:30,13/Nov | 42 | 19:30,18/Jul | 12
[14 empty] | 5BFLOOR 1TMY15WA | 5B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,03/Jun | 38 | 04:30,24/Dec | 13
[14 empty] | 5BMECHTMY15WA | 5B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,03/Sep | 17
[14 empty] | 5BFLOOR 2TMY15WA | 5B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 06:30,23/Aug | 46 | 14:30,25/Jul | 15
[14 empty] | 5BAUDITORIUMTMY15WA | 5B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 18:30,08/Jan | 49 | 14:30,25/Jul | 14
[14 empty] | 5BGYMTMY15WA | 5B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 11:30,31/Dec | 54 | 18:30,28/May | 12
[14 empty] | 5BKITCHEN CAFETERIATMY15WA | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 12:30,21/Mar | 38 | 04:30,24/Dec | 11
[14 empty] | 5BFLOOR 1MIN | 5B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,12/Jul | 45 | 04:30,06/Dec | 18
[14 empty] | 5BMECHMIN | 5B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 22:30,12/Aug | 51 | 05:30,02/Feb | 21
[14 empty] | 5BFLOOR 2MIN | 5B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,20/Jul | 44 | 04:30,02/Feb | 18
[14 empty] | 5BAUDITORIUMMIN | 5B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 16:30,05/Mar | 48 | 03:30,06/Dec | 18
[14 empty] | 5BGYMMIN | 5B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,17/Nov | 48 | 04:30,06/Dec | 13
[14 empty] | 5BKITCHEN CAFETERIAMIN | 5B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 20:30,14/Jun | 41 | 05:30,06/Dec | 13
[14 empty] | 5BFLOOR 1MAX | 5B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 06:30,05/May | 38 | 15:30,25/Jul | 13
[14 empty] | 5BMECHMAX | 5B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 09:30,20/Apr | 64 | 15:30,03/Sep | 20
[14 empty] | 5BFLOOR 2MAX | 5B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,23/Sep | 48 | 14:30,25/Jul | 15
[14 empty] | 5BAUDITORIUMMAX | 5B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 13:30,07/Dec | 50 | 12:30,25/Jul | 13
[14 empty] | 5BGYMMAX | 5B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 11:30,03/Apr | 63 | 18:30,31/May | 14
[14 empty] | 5BKITCHEN CAFETERIAMAX | 5B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 17:30,02/Feb | 35 | 18:30,25/Jul | 11
[14 empty] | 5CLocationFilename | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 5CFLOOR 1TMY7WA | 5C | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 07:30,07/Oct | 30 | 04:30,04/Jan | 11
[14 empty] | 5CMECHTMY7WA | 5C | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 23:30,24/Jun | 36 | 16:30,15/Sep | 12
[14 empty] | 5CFLOOR 2TMY7WA | 5C | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,04/Oct | 36 | 15:30,18/Jul | 12
[14 empty] | 5CAUDITORIUMTMY7WA | 5C | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 10:30,12/Apr | 40 | 00:30,01/Feb | 11
[14 empty] | 5CGYMTMY7WA | 5C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 07:30,24/May | 36 | 17:30,15/Sep | 9
[14 empty] | 5CKITCHEN CAFETERIATMY7WA | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 17:30,06/Dec | 25 | 10:30,07/Sep | 8
[14 empty] | 5CFLOOR 1TMY3WA | 5C | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,17/May | 28 | 04:30,27/Dec | 10
[14 empty] | 5CMECHTMY3WA | 5C | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 22:30,08/May | 48 | 18:30,28/May | 11
[14 empty] | 5CFLOOR 2TMY3WA | 5C | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,28/Oct | 46 | 15:30,25/Jul | 12
[14 empty] | 5CAUDITORIUMTMY3WA | 5C | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 12:30,15/Jan | 32 | 16:30,25/Jul | 11
[14 empty] | 5CGYMTMY3WA | 5C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 14:30,20/Mar | 61 | 18:30,28/May | 9
[14 empty] | 5CKITCHEN CAFETERIATMY3WA | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 17:30,07/Dec | 30 | 10:30,09/Sep | 9
[14 empty] | 5CFLOOR 1TMY2 | 5C | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 06:30,16/Jun | 45 | 12:30,18/Jul | 15
[14 empty] | 5CMECHTMY2 | 5C | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 10:30,09/Oct | 62 | 17:30,20/Jul | 19
[14 empty] | 5CFLOOR 2TMY2 | 5C | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,30/Apr | 53 | 15:30,18/Jul | 17
[14 empty] | 5CAUDITORIUMTMY2 | 5C | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 14:30,11/Oct | 63 | 14:30,18/Jul | 16
[14 empty] | 5CGYMTMY2 | 5C | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 12:30,26/Sep | 49 | 01:30,08/Mar | 11
[14 empty] | 5CKITCHEN CAFETERIATMY2 | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 17:30,16/Nov | 51 | 04:30,21/Jul | 13
[14 empty] | 5CFLOOR 1TMY15WA | 5C | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,29/Apr | 30 | 15:30,11/Jul | 10
[14 empty] | 5CMECHTMY15WA | 5C | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 23:30,18/Jun | 36 | 15:30,11/Jul | 11
[14 empty] | 5CFLOOR 2TMY15WA | 5C | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,29/Sep | 52 | 14:30,11/Jul | 12
[14 empty] | 5CAUDITORIUMTMY15WA | 5C | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 11:30,01/Apr | 50 | 14:30,11/Jul | 11
[14 empty] | 5CGYMTMY15WA | 5C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 07:30,24/May | 31 | 23:30,31/Oct | 9
[14 empty] | 5CKITCHEN CAFETERIATMY15WA | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 16:30,04/Nov | 32 | 19:30,11/Jul | 8
[14 empty] | 5CFLOOR 1MIN | 5C | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,27/Aug | 39 | 03:30,20/Dec | 14
[14 empty] | 5CMECHMIN | 5C | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 23:30,03/Sep | 46 | 05:30,20/Dec | 16
[14 empty] | 5CFLOOR 2MIN | 5C | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,27/Aug | 38 | 03:30,04/Jan | 14
[14 empty] | 5CAUDITORIUMMIN | 5C | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 12:30,15/Apr | 43 | 16:30,07/Feb | 15
[14 empty] | 5CGYMMIN | 5C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 15:30,15/Jan | 46 | 05:30,20/Dec | 10
[14 empty] | 5CKITCHEN CAFETERIAMIN | 5C | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 19:30,01/Apr | 38 | 02:30,20/Dec | 9
[14 empty] | 5CFLOOR 1MAX | 5C | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,29/Apr | 31 | 15:30,11/Jul | 10
[14 empty] | 5CMECHMAX | 5C | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 15:30,17/Oct | 56 | 19:30,28/May | 13
[14 empty] | 5CFLOOR 2MAX | 5C | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,08/Apr | 53 | 14:30,11/Jul | 13
[14 empty] | 5CAUDITORIUMMAX | 5C | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 21:30,12/Mar | 52 | 18:30,11/Jul | 11
[14 empty] | 5CGYMMAX | 5C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 13:30,24/Oct | 64 | 19:30,28/May | 9
[14 empty] | 5CKITCHEN CAFETERIAMAX | 5C | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 13:30,24/Oct | 38 | 19:30,11/Jul | 10
[14 empty] | 5CFLOOR 1doeCWEC | 5C | People dissatisfied | FLOOR 1 | doeCWEC | Percentage (%) | 5 | 07:30,14/May | 34 | 04:30,22/Nov | 11
[14 empty] | 5CMECHdoeCWEC | 5C | People dissatisfied | MECH | doeCWEC | Percentage (%) | 5 | 01:30,16/Oct | 33 | 04:30,22/Nov | 12
[14 empty] | 5CFLOOR 2doeCWEC | 5C | People dissatisfied | FLOOR 2 | doeCWEC | Percentage (%) | 5 | 07:30,22/Oct | 42 | 16:30,11/Jul | 12
[14 empty] | 5CAUDITORIUMdoeCWEC | 5C | People dissatisfied | AUDITORIUM | doeCWEC | Percentage (%) | 5 | 07:30,08/Jul | 43 | 03:30,22/Nov | 11
[14 empty] | 5CGYMdoeCWEC | 5C | People dissatisfied | GYM | doeCWEC | Percentage (%) | 5 | 15:30,02/May | 34 | 03:30,22/Nov | 9
[14 empty] | 5CKITCHEN CAFETERIAdoeCWEC | 5C | People dissatisfied | KITCHEN CAFETERIA | doeCWEC | Percentage (%) | 5 | 19:30,29/Oct | 26 | 04:30,22/Nov | 9
[14 empty] | 5CFLOOR 1CWEC | 5C | People dissatisfied | FLOOR 1 | CWEC | Percentage (%) | 5 | 07:30,14/May | 33 | 03:30,22/Nov | 11
[14 empty] | 5CMECHCWEC | 5C | People dissatisfied | MECH | CWEC | Percentage (%) | 5 | 01:30,16/Oct | 33 | 04:30,22/Nov | 12
[14 empty] | 5CFLOOR 2CWEC | 5C | People dissatisfied | FLOOR 2 | CWEC | Percentage (%) | 5 | 07:30,22/Oct | 41 | 15:30,11/Jul | 12
[14 empty] | 5CAUDITORIUMCWEC | 5C | People dissatisfied | AUDITORIUM | CWEC | Percentage (%) | 5 | 21:30,10/Mar | 43 | 03:30,22/Nov | 11
[14 empty] | 5CGYMCWEC | 5C | People dissatisfied | GYM | CWEC | Percentage (%) | 5 | 15:30,02/May | 34 | 03:30,22/Nov | 9
[14 empty] | 5CKITCHEN CAFETERIACWEC | 5C | People dissatisfied | KITCHEN CAFETERIA | CWEC | Percentage (%) | 5 | 16:30,24/Dec | 26 | 04:30,22/Nov | 9
[14 empty] | 6ALocationFilename | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 6AFLOOR 1TMY7WA | 6A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,13/May | 45 | 13:30,04/Jul | 15
[14 empty] | 6AMECHTMY7WA | 6A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 22:30,04/Oct | 67 | 17:30,09/Sep | 21
[14 empty] | 6AFLOOR 2TMY7WA | 6A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,13/Oct | 58 | 13:30,08/Aug | 17
[14 empty] | 6AAUDITORIUMTMY7WA | 6A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 01:30,03/Sep | 63 | 17:30,04/Jul | 16
[14 empty] | 6AGYMTMY7WA | 6A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 09:30,22/Mar | 48 | 05:30,24/Jan | 11
[14 empty] | 6AKITCHEN CAFETERIATMY7WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 19:30,03/Nov | 48 | 19:30,04/Jul | 14
[14 empty] | 6AFLOOR 1TMY3WA | 6A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,21/Apr | 52 | 11:30,18/Jul | 15
[14 empty] | 6AMECHTMY3WA | 6A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 15:30,07/Nov | 68 | 18:30,18/Jul | 21
[14 empty] | 6AFLOOR 2TMY3WA | 6A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,16/Apr | 59 | 11:30,18/Jul | 17
[14 empty] | 6AAUDITORIUMTMY3WA | 6A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 19:30,23/Feb | 65 | 12:30,17/Jul | 16
[14 empty] | 6AGYMTMY3WA | 6A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 13:30,13/Mar | 49 | 17:30,21/May | 11
[14 empty] | 6AKITCHEN CAFETERIATMY3WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 15:30,24/Oct | 59 | 19:30,18/Jul | 14
[14 empty] | 6AFLOOR 1TMY3 | 6A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 06:30,07/May | 50 | 12:30,04/Jul | 16
[14 empty] | 6AMECHTMY3 | 6A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 01:30,05/May | 65 | 17:30,19/Jul | 21
[14 empty] | 6AFLOOR 2TMY3 | 6A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,19/Apr | 56 | 15:30,18/Jul | 18
[14 empty] | 6AAUDITORIUMTMY3 | 6A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 20:30,01/Dec | 64 | 14:30,01/Aug | 17
[14 empty] | 6AGYMTMY3 | 6A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,20/Dec | 50 | 04:30,31/Jan | 12
[14 empty] | 6AKITCHEN CAFETERIATMY3 | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 17:30,01/Mar | 57 | 20:30,18/Jul | 14
[14 empty] | 6AFLOOR 1TMY2 | 6A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,10/May | 47 | 12:30,18/Jul | 16
[14 empty] | 6AMECHTMY2 | 6A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 15:30,03/Oct | 64 | 18:30,28/May | 21
[14 empty] | 6AFLOOR 2TMY2 | 6A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,26/Mar | 52 | 17:30,18/Jul | 18
[14 empty] | 6AAUDITORIUMTMY2 | 6A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 16:30,16/Mar | 61 | 16:30,17/Jul | 16
[14 empty] | 6AGYMTMY2 | 6A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 15:30,25/Sep | 48 | 07:30,10/Jan | 12
[14 empty] | 6AKITCHEN CAFETERIATMY2 | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 17:30,19/Nov | 49 | 07:30,18/Jul | 14
[14 empty] | 6AFLOOR 1TMY15WA | 6A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,13/May | 50 | 17:30,04/Jul | 15
[14 empty] | 6AMECHTMY15WA | 6A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 04:30,06/Oct | 66 | 18:30,04/Jul | 22
[14 empty] | 6AFLOOR 2TMY15WA | 6A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,13/Oct | 58 | 15:30,03/Jul | 17
[14 empty] | 6AAUDITORIUMTMY15WA | 6A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 21:30,08/Apr | 61 | 11:30,08/Aug | 16
[14 empty] | 6AGYMTMY15WA | 6A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,24/Mar | 42 | 19:30,04/Jul | 12
[14 empty] | 6AKITCHEN CAFETERIATMY15WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 13:30,02/Oct | 57 | 19:30,04/Jul | 14
[14 empty] | 6AFLOOR 1MIN | 6A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,25/Jun | 44 | 04:30,01/Feb | 17
[14 empty] | 6AMECHMIN | 6A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 08:30,28/Jun | 45 | 06:30,21/Jan | 21
[14 empty] | 6AFLOOR 2MIN | 6A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,25/Jun | 44 | 04:30,21/Jan | 18
[14 empty] | 6AAUDITORIUMMIN | 6A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 12:30,17/May | 51 | 05:30,01/Feb | 17
[14 empty] | 6AGYMMIN | 6A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,15/Mar | 49 | 06:30,03/Jan | 12
[14 empty] | 6AKITCHEN CAFETERIAMIN | 6A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 15:30,26/Sep | 40 | 04:30,31/Jan | 13
[14 empty] | 6AFLOOR 1MAX | 6A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,08/Apr | 58 | 19:30,18/Jul | 18
[14 empty] | 6AMECHMAX | 6A | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 09:30,26/Nov | 85 | 19:30,18/Jul | 29
[14 empty] | 6AFLOOR 2MAX | 6A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,15/Oct | 60 | 17:30,18/Jul | 20
[14 empty] | 6AAUDITORIUMMAX | 6A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 14:30,08/Jan | 65 | 13:30,18/Jul | 18
[14 empty] | 6AGYMMAX | 6A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,03/Mar | 63 | 05:30,19/Jul | 14
[14 empty] | 6AKITCHEN CAFETERIAMAX | 6A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 13:30,20/Nov | 60 | 18:30,18/Jul | 17
[14 empty] | 6BLocationFilename | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 6BFLOOR 1TMY7WA | 6B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 10 | 07:30,23/Jul | 63 | 04:30,10/May | 36
[14 empty] | 6BMECHTMY7WA | 6B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 32 | 07:30,19/Jan | 93 | 19:30,07/Apr | 65
[14 empty] | 6BFLOOR 2TMY7WA | 6B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 8 | 07:30,19/Jan | 60 | 03:30,05/Apr | 37
[14 empty] | 6BAUDITORIUMTMY7WA | 6B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 11 | 21:30,24/Dec | 78 | 18:30,24/May | 37
[14 empty] | 6BGYMTMY7WA | 6B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 9 | 08:30,19/Jan | 54 | 05:30,06/Apr | 22
[14 empty] | 6BKITCHEN CAFETERIATMY7WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 15 | 07:30,28/Jul | 84 | 13:30,03/Sep | 38
[14 empty] | 6BFLOOR 1TMY3WA | 6B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,02/Jun | 38 | 17:30,18/Jul | 14
[14 empty] | 6BMECHTMY3WA | 6B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 23:30,07/Oct | 63 | 16:30,22/Jul | 18
[14 empty] | 6BFLOOR 2TMY3WA | 6B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,27/May | 53 | 15:30,25/Jul | 15
[14 empty] | 6BAUDITORIUMTMY3WA | 6B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 03:30,11/Jul | 52 | 16:30,18/Jul | 15
[14 empty] | 6BGYMTMY3WA | 6B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 13:30,15/Mar | 59 | 18:30,01/Sep | 13
[14 empty] | 6BKITCHEN CAFETERIATMY3WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 16:30,22/Mar | 39 | 19:30,18/Jul | 11
[14 empty] | 6BFLOOR 1TMY3 | 6B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,20/May | 40 | 01:30,27/Dec | 13
[14 empty] | 6BMECHTMY3 | 6B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 09:30,15/May | 55 | 17:30,15/Sep | 18
[14 empty] | 6BFLOOR 2TMY3 | 6B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,22/Jun | 50 | 15:30,08/Aug | 15
[14 empty] | 6BAUDITORIUMTMY3 | 6B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 20:30,03/Dec | 47 | 16:30,08/Aug | 14
[14 empty] | 6BGYMTMY3 | 6B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 14:30,22/Jan | 58 | 18:30,25/May | 12
[14 empty] | 6BKITCHEN CAFETERIATMY3 | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 16:30,08/Mar | 39 | 01:30,18/Jan | 11
[14 empty] | 6BFLOOR 1TMY2 | 6B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,11/Jun | 43 | 05:30,12/Dec | 14
[14 empty] | 6BMECHTMY2 | 6B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 01:30,18/Jun | 57 | 15:30,30/Jun | 18
[14 empty] | 6BFLOOR 2TMY2 | 6B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,01/Sep | 48 | 15:30,26/Jun | 15
[14 empty] | 6BAUDITORIUMTMY2 | 6B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 11:30,20/Apr | 50 | 06:30,12/Dec | 15
[14 empty] | 6BGYMTMY2 | 6B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,05/Oct | 54 | 17:30,02/Sep | 12
[14 empty] | 6BKITCHEN CAFETERIATMY2 | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 18:30,30/Dec | 40 | 05:30,13/Dec | 11
[14 empty] | 6BFLOOR 1TMY15WA | 6B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,17/Jun | 35 | 04:30,30/Dec | 13
[14 empty] | 6BMECHTMY15WA | 6B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 08:30,23/Jun | 57 | 14:30,29/Jul | 17
[14 empty] | 6BFLOOR 2TMY15WA | 6B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,24/Sep | 46 | 14:30,25/Jul | 15
[14 empty] | 6BAUDITORIUMTMY15WA | 6B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 18:30,12/Jan | 50 | 14:30,24/Jul | 14
[14 empty] | 6BGYMTMY15WA | 6B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,24/May | 58 | 18:30,02/Sep | 12
[14 empty] | 6BKITCHEN CAFETERIATMY15WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 12:30,16/Oct | 37 | 05:30,30/Dec | 10
[14 empty] | 6BFLOOR 1MIN | 6B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,11/Aug | 43 | 04:30,06/Dec | 18
[14 empty] | 6BMECHMIN | 6B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 22:30,11/Aug | 48 | 06:30,17/Feb | 23
[14 empty] | 6BFLOOR 2MIN | 6B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,11/Aug | 45 | 04:30,17/Feb | 19
[14 empty] | 6BAUDITORIUMMIN | 6B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 17:30,04/Mar | 50 | 04:30,20/Dec | 19
[14 empty] | 6BGYMMIN | 6B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 17:30,08/Jun | 49 | 02:30,05/Dec | 13
[14 empty] | 6BKITCHEN CAFETERIAMIN | 6B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 10:30,04/Sep | 42 | 05:30,18/Feb | 14
[14 empty] | 6BFLOOR 1MAX | 6B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 06:30,12/May | 40 | 13:30,01/Aug | 13
[14 empty] | 6BMECHMAX | 6B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 22:30,28/Oct | 68 | 14:30,16/Jul | 20
[14 empty] | 6BFLOOR 2MAX | 6B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,21/Sep | 50 | 12:30,01/Aug | 15
[14 empty] | 6BAUDITORIUMMAX | 6B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 19:30,09/Feb | 49 | 13:30,18/Jul | 14
[14 empty] | 6BGYMMAX | 6B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 13:30,13/Mar | 65 | 18:30,03/Sep | 15
[14 empty] | 6BKITCHEN CAFETERIAMAX | 6B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 11:30,06/Nov | 41 | 19:30,01/Aug | 11
[14 empty] | 7LocationFilename | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 7FLOOR 1TMY7WA | 7 | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 07:30,22/Sep | 42 | 13:30,04/Jul | 15
[14 empty] | 7MECHTMY7WA | 7 | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 23:30,06/Oct | 55 | 14:30,07/Sep | 19
[14 empty] | 7FLOOR 2TMY7WA | 7 | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,21/Sep | 51 | 15:30,04/Jul | 16
[14 empty] | 7AUDITORIUMTMY7WA | 7 | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 10:30,20/Oct | 59 | 16:30,04/Jul | 15
[14 empty] | 7GYMTMY7WA | 7 | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 11:30,19/Jan | 46 | 07:30,03/Jan | 11
[14 empty] | 7KITCHEN CAFETERIATMY7WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 18:30,02/Nov | 46 | 07:30,04/Jul | 13
[14 empty] | 7FLOOR 1TMY3WA | 7 | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 06:30,25/May | 47 | 16:30,04/Jul | 14
[14 empty] | 7MECHTMY3WA | 7 | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 22:30,13/May | 58 | 15:30,31/May | 18
[14 empty] | 7FLOOR 2TMY3WA | 7 | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,24/Mar | 57 | 16:30,04/Jul | 16
[14 empty] | 7AUDITORIUMTMY3WA | 7 | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 13:30,07/Apr | 60 | 11:30,04/Jul | 15
[14 empty] | 7GYMTMY3WA | 7 | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 11:30,25/Jan | 49 | 17:30,05/May | 11
[14 empty] | 7KITCHEN CAFETERIATMY3WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 17:30,22/Nov | 48 | 07:30,04/Jul | 12
[14 empty] | 7FLOOR 1TMY3 | 7 | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,12/May | 42 | 03:30,20/Dec | 15
[14 empty] | 7MECHTMY3 | 7 | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 23:30,29/Sep | 44 | 16:30,26/May | 19
[14 empty] | 7FLOOR 2TMY3 | 7 | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,10/Sep | 54 | 14:30,17/Jul | 16
[14 empty] | 7AUDITORIUMTMY3 | 7 | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 20:30,22/Mar | 57 | 16:30,18/Jul | 16
[14 empty] | 7GYMTMY3 | 7 | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,26/Feb | 49 | 00:30,20/Dec | 11
[14 empty] | 7KITCHEN CAFETERIATMY3 | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 18:30,13/Apr | 45 | 18:30,18/Jul | 12
[14 empty] | 7FLOOR 1TMY2 | 7 | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,24/Jun | 43 | 04:30,01/Feb | 15
[14 empty] | 7MECHTMY2 | 7 | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 21:30,05/Jun | 47 | 16:30,08/Jul | 19
[14 empty] | 7FLOOR 2TMY2 | 7 | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,23/Jun | 50 | 16:30,11/Jul | 16
[14 empty] | 7AUDITORIUMTMY2 | 7 | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 09:30,12/May | 51 | 05:30,08/Feb | 16
[14 empty] | 7GYMTMY2 | 7 | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 14:30,12/Feb | 49 | 01:30,01/Feb | 11
[14 empty] | 7KITCHEN CAFETERIATMY2 | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 19:30,02/Nov | 43 | 20:30,11/Jul | 12
[14 empty] | 7FLOOR 1TMY15WA | 7 | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,15/Oct | 51 | 10:30,18/Jul | 14
[14 empty] | 7MECHTMY15WA | 7 | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 23:30,15/Apr | 60 | 12:30,18/Jul | 18
[14 empty] | 7FLOOR 2TMY15WA | 7 | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,30/Sep | 57 | 12:30,18/Jul | 16
[14 empty] | 7AUDITORIUMTMY15WA | 7 | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 20:30,19/Feb | 65 | 12:30,17/Jul | 15
[14 empty] | 7GYMTMY15WA | 7 | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 11:30,01/Mar | 37 | 05:30,25/Jan | 11
[14 empty] | 7KITCHEN CAFETERIATMY15WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 12:30,13/Nov | 53 | 07:30,18/Jul | 13
[14 empty] | 7FLOOR 1MIN | 7 | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,20/Aug | 45 | 18:30,17/Jan | 17
[14 empty] | 7MECHMIN | 7 | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 09:30,12/Aug | 47 | 19:30,17/Jan | 21
[14 empty] | 7FLOOR 2MIN | 7 | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,27/Jul | 46 | 07:30,17/Jan | 18
[14 empty] | 7AUDITORIUMMIN | 7 | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 19:30,26/Mar | 51 | 22:30,17/Jan | 18
[14 empty] | 7GYMMIN | 7 | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 16:30,23/Mar | 49 | 07:30,17/Jan | 12
[14 empty] | 7KITCHEN CAFETERIAMIN | 7 | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 16:30,07/Oct | 43 | 22:30,17/Jan | 13
[14 empty] | 7FLOOR 1MAX | 7 | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,26/Apr | 56 | 09:30,18/Jul | 16
[14 empty] | 7MECHMAX | 7 | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 23:30,11/Apr | 73 | 13:30,18/Jul | 24
[14 empty] | 7FLOOR 2MAX | 7 | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,15/Oct | 59 | 13:30,18/Jul | 18
[14 empty] | 7AUDITORIUMMAX | 7 | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 13:30,05/Apr | 64 | 10:30,18/Jul | 16
[14 empty] | 7GYMMAX | 7 | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,13/Mar | 50 | 17:30,29/Sep | 12
[14 empty] | 7KITCHEN CAFETERIAMAX | 7 | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 15:30,03/Apr | 56 | 19:30,18/Jul | 15
[14 empty] | 8LocationFilename | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[14 empty] | 8FLOOR 1TMY7WA | 8 | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,20/Aug | 44 | 03:30,28/Jan | 16
[14 empty] | 8MECHTMY7WA | 8 | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 00:30,04/Sep | 45 | 04:30,28/Jan | 20
[14 empty] | 8FLOOR 2TMY7WA | 8 | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,26/Jan | 17
[14 empty] | 8AUDITORIUMTMY7WA | 8 | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 23:30,19/May | 48 | 05:30,19/Dec | 16
[14 empty] | 8GYMTMY7WA | 8 | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 10:30,13/Jun | 55 | 19:30,26/May | 12
[14 empty] | 8KITCHEN CAFETERIATMY7WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 17:30,02/Apr | 43 | 20:30,27/Jan | 13
[14 empty] | 8FLOOR 1TMY3WA | 8 | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 06:30,02/Sep | 42 | 00:30,06/Dec | 15
[14 empty] | 8MECHTMY3WA | 8 | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 00:30,11/Sep | 54 | 16:30,28/Jun | 20
[14 empty] | 8FLOOR 2TMY3WA | 8 | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,27/Aug | 51 | 15:30,19/Jun | 17
[14 empty] | 8AUDITORIUMTMY3WA | 8 | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 10:30,28/Apr | 50 | 15:30,19/Jun | 16
[14 empty] | 8GYMTMY3WA | 8 | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 14:30,05/Mar | 52 | 18:30,12/May | 12
[14 empty] | 8KITCHEN CAFETERIATMY3WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 17:30,08/Apr | 41 | 21:30,27/Jun | 12
[14 empty] | 8FLOOR 1TMY3 | 8 | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,19/May | 44 | 04:30,01/Mar | 16
[14 empty] | 8MECHTMY3 | 8 | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 22:30,19/Aug | 45 | 04:30,01/Mar | 21
[14 empty] | 8FLOOR 2TMY3 | 8 | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,12/Jan | 18
[14 empty] | 8AUDITORIUMTMY3 | 8 | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 16:30,11/Mar | 52 | 04:30,01/Mar | 17
[14 empty] | 8GYMTMY3 | 8 | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 10:30,21/Aug | 50 | 20:30,05/Dec | 12
[14 empty] | 8KITCHEN CAFETERIATMY3 | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 17:30,29/Sep | 41 | 02:30,01/Mar | 14
[14 empty] | 8FLOOR 1TMY2 | 8 | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,03/Jun | 49 | 04:30,04/Jan | 17
[14 empty] | 8MECHTMY2 | 8 | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 09:30,13/Jun | 50 | 05:30,04/Jan | 21
[14 empty] | 8FLOOR 2TMY2 | 8 | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,27/Aug | 49 | 01:30,04/Jan | 18
[14 empty] | 8AUDITORIUMTMY2 | 8 | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 13:30,18/May | 55 | 01:30,04/Jan | 18
[14 empty] | 8GYMTMY2 | 8 | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 15:30,19/Mar | 52 | 04:30,03/Jan | 12
[14 empty] | 8KITCHEN CAFETERIATMY2 | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 20:30,22/Apr | 47 | 05:30,04/Jan | 14
[14 empty] | 8FLOOR 1TMY15WA | 8 | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,21/May | 40 | 06:30,21/Feb | 16
[14 empty] | 8MECHTMY15WA | 8 | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 09:30,23/Sep | 54 | 16:30,28/Jun | 20
[14 empty] | 8FLOOR 2TMY15WA | 8 | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,22/Sep | 51 | 15:30,19/Jun | 17
[14 empty] | 8AUDITORIUMTMY15WA | 8 | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 18:30,12/Feb | 50 | 15:30,19/Jun | 16
[14 empty] | 8GYMTMY15WA | 8 | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 10:30,28/Oct | 47 | 04:30,21/Feb | 12
[14 empty] | 8KITCHEN CAFETERIATMY15WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 17:30,07/Apr | 41 | 21:30,27/Jun | 13
[14 empty] | 8FLOOR 1MIN | 8 | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,02/Jul | 49 | 03:30,18/Jan | 21
[14 empty] | 8MECHMIN | 8 | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 11:30,15/Jul | 51 | 06:30,11/Jan | 26
[14 empty] | 8FLOOR 2MIN | 8 | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,16/Jul | 50 | 04:30,11/Jan | 21
[14 empty] | 8AUDITORIUMMIN | 8 | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 13:30,03/Sep | 56 | 05:30,11/Jan | 22
[14 empty] | 8GYMMIN | 8 | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 12:30,12/Oct | 52 | 04:30,01/Feb | 14
[14 empty] | 8KITCHEN CAFETERIAMIN | 8 | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 17:30,31/Aug | 47 | 05:30,11/Jan | 16
[14 empty] | 8FLOOR 1MAX | 8 | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,24/Sep | 40 | 20:30,27/Jun | 15
[14 empty] | 8MECHMAX | 8 | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 01:30,02/Oct | 68 | 18:30,28/May | 20
[14 empty] | 8FLOOR 2MAX | 8 | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,31/Aug | 51 | 15:30,20/Jun | 17
[14 empty] | 8AUDITORIUMMAX | 8 | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 10:30,08/Oct | 50 | 16:30,03/Jul | 15
[14 empty] | 8GYMMAX | 8 | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,12/Sep | 66 | 18:30,25/May | 14
[14 empty] | 8KITCHEN CAFETERIAMAX | 8 | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 14:30,09/Oct | 45 | 22:30,27/Jun | 12

## 3s Summary of Results
| Building Area (ft2): | 211975
1A - Miami | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5549883 | 3460491 | 1892969 | 175825 | 1213937 | 5197836 | 0 | 220882 | 345722 | 34299 | 1228691 | 18091844 | 85.349 | max EUI | max EUI
| TMY3 DOE | 5571522 | 3614661 | 1892969 | 178641 | 1213937 | 5188993 | 0 | 230723 | 345722 | 34299 | 1228691 | 18271467 | 86.1963 | 88.5468 | 86.462
| TMY3 WA | 4729115 | 4333478 | 1892969 | 180906 | 1213937 | 5320743 | 0 | 276605 | 345722 | 34299 | 1228691 | 18327774 | 86.462 | min EUI | min EUI
| TMY7 WA | 5060353 | 3855137 | 1892969 | 182207 | 1213937 | 5243826 | 0 | 246073 | 345722 | 34299 | 1228691 | 18074523 | 85.2672 | 84.0488 | 84.0488
| TMY15 WA | 4642740 | 3973030 | 1892969 | 181525 | 1213937 | 5278428 | 0 | 253598 | 345722 | 34299 | 1228691 | 17816248 | 84.0488 | variance | variance
| XMY Min WA | 7624176 | 2556310 | 1892969 | 183602 | 1213937 | 4755530 | 0 | 163169 | 345722 | 34299 | 1228691 | 18769714 | 88.5468 | 5.218% | 2.8%
| XMY Max WA | 4263211 | 4720237 | 1892969 | 178359 | 1213937 | 5356205 | 0 | 301292 | 345722 | 34299 | 1228691 | 18306231 | 86.3603
2A - Houston | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5918441 | 2654814 | 1892969 | 177640 | 1213937 | 4642941 | 0 | 169456 | 345722 | 34299 | 1228691 | 17050219 | 80.435 | max EUI | max EUI
| TMY3 DOE | 5737468 | 2685074 | 1892969 | 179554 | 1213937 | 4680181 | 0 | 171388 | 345722 | 34299 | 1228691 | 16940592 | 79.9179 | 87.9067 | 80.435
| TMY3 WA | 4005799 | 3216642 | 1892969 | 186049 | 1213937 | 4830757 | 0 | 205318 | 345722 | 34299 | 1228691 | 15931492 | 75.1574 | min EUI | min EUI
| TMY7 WA | 4693749 | 2964545 | 1892969 | 186368 | 1213937 | 4774639 | 0 | 189226 | 345722 | 34299 | 1228691 | 16295454 | 76.8744 | 73.2895 | 75.1574
| TMY15 WA | 4642168 | 3087800 | 1892969 | 185961 | 1213937 | 4803415 | 0 | 197094 | 345722 | 34299 | 1228691 | 16403365 | 77.3835 | variance | variance
| XMY Min WA | 8955406 | 1758005 | 1892969 | 195846 | 1213937 | 4125621 | 0 | 112213 | 345722 | 34299 | 1228691 | 18634018 | 87.9067 | 18.29% | 6.604%
| XMY Max WA | 2745476 | 3868301 | 1892969 | 183590 | 1213937 | 5004342 | 0 | 246913 | 345722 | 34299 | 1228691 | 15535549 | 73.2895
2B - Phoenix | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 3953610 | 2499860 | 1892969 | 175394 | 1213937 | 5536467 | 0 | 159566 | 345722 | 34299 | 1228691 | 15811824 | 74.5929 | max EUI | max EUI
| TMY3 DOE | 3585293 | 2713268 | 1892969 | 177114 | 1213937 | 5614091 | 0 | 173187 | 345722 | 34299 | 1228691 | 15749880 | 74.3006 | 79.8089 | 74.5929
| TMY3 WA | 3107419 | 2699997 | 1892969 | 181625 | 1213937 | 5572222 | 0 | 172340 | 345722 | 34299 | 1228691 | 15220530 | 71.8034 | min EUI | min EUI
| TMY7 WA | 3407359 | 2374687 | 1892969 | 180843 | 1213937 | 5553422 | 0 | 151576 | 345722 | 34299 | 1228691 | 15154814 | 71.4934 | 70.5438 | 71.4934
| TMY15 WA | 3329373 | 2545343 | 1892969 | 181125 | 1213937 | 5525664 | 0 | 162469 | 345722 | 34299 | 1228691 | 15230901 | 71.8523 | variance | variance
| XMY Min WA | 6716371 | 1399314 | 1892969 | 181419 | 1213937 | 5044141 | 0 | 89318 | 345722 | 34299 | 1228691 | 16917490 | 79.8089 | 12.47% | 4.172%
| XMY Max WA | 2095227 | 3278823 | 1892969 | 179385 | 1213937 | 5703871 | 0 | 209287 | 345722 | 34299 | 1228691 | 14953520 | 70.5438
3A - Atlanta | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 7732370 | 1597327 | 1892969 | 177771 | 1213937 | 4251719 | 0 | 101957 | 345722 | 34299 | 1228691 | 17348071 | 81.8402 | max EUI | max EUI
| TMY3 DOE | 7323336 | 1717807 | 1892969 | 180756 | 1213937 | 4292979 | 0 | 109647 | 345722 | 34299 | 1228691 | 17111452 | 80.7239 | 92.9901 | 81.8402
| TMY3 WA | 6052703 | 2099635 | 1892969 | 188858 | 1213937 | 4430086 | 0 | 134019 | 345722 | 34299 | 1228691 | 16392228 | 77.3309 | min EUI | min EUI
| TMY7 WA | 6668815 | 1895825 | 1892969 | 189208 | 1213937 | 4324125 | 0 | 121010 | 345722 | 34299 | 1228691 | 16685910 | 78.7164 | 71.775 | 76.9473
| TMY15 WA | 6157000 | 1958595 | 1892969 | 188094 | 1213937 | 4395270 | 0 | 125017 | 345722 | 34299 | 1228691 | 16310903 | 76.9473 | variance | variance
| XMY Min WA | 11225021 | 927854 | 1892969 | 187506 | 1213937 | 3825035 | 0 | 59225 | 345722 | 34299 | 1228691 | 19711568 | 92.9901 | 26.28% | 6.061%
| XMY Max WA | 4101380 | 2628214 | 1892969 | 189433 | 1213937 | 4640804 | 0 | 167758 | 345722 | 34299 | 1228691 | 15214516 | 71.775
3B - Las Vegas | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5400741 | 1692105 | 1892969 | 174724 | 1213937 | 5045342 | 0 | 108007 | 345722 | 34299 | 1228691 | 15907846 | 75.0459 | max EUI | max EUI
| TMY3 DOE | 5367329 | 1780729 | 1892969 | 177559 | 1213937 | 5048687 | 0 | 113664 | 345722 | 34299 | 1228691 | 15974895 | 75.3622 | 83.8495 | 75.3622
| TMY3 WA | 4753096 | 1891425 | 1892969 | 180956 | 1213937 | 5032802 | 0 | 120729 | 345722 | 34299 | 1228691 | 15465935 | 72.9611 | min EUI | min EUI
| TMY7 WA | 4993446 | 1686900 | 1892969 | 180831 | 1213937 | 5024264 | 0 | 107674 | 345722 | 34299 | 1228691 | 15480042 | 73.0277 | 70.1901 | 72.9611
| TMY15 WA | 5044383 | 1727406 | 1892969 | 180906 | 1213937 | 5010962 | 0 | 110260 | 345722 | 34299 | 1228691 | 15560844 | 73.4089 | variance | variance
| XMY Min WA | 8732102 | 800650 | 1892969 | 180599 | 1213937 | 4522612 | 0 | 51105 | 345722 | 34299 | 1228691 | 17773995 | 83.8495 | 18.12% | 3.186%
| XMY Max WA | 3393126 | 2458393 | 1892969 | 179980 | 1213937 | 5203212 | 0 | 156919 | 345722 | 34299 | 1228691 | 14878557 | 70.1901
3C - San Francisco | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 9047897 | 672293 | 1892969 | 179911 | 1213937 | 3940385 | 0 | 42912 | 345722 | 34299 | 1228691 | 17370325 | 81.9452 | max EUI | max EUI
| TMY3 DOE | 8637653 | 749649 | 1892969 | 181650 | 1213937 | 4009935 | 0 | 47850 | 345722 | 34299 | 1228691 | 17113664 | 80.7344 | 88.7546 | 82.6112
| TMY3 WA | 7508169 | 825020 | 1892969 | 185980 | 1213937 | 4110782 | 0 | 52661 | 345722 | 34299 | 1228691 | 16169539 | 76.2804 | min EUI | min EUI
| TMY7 WA | 9087022 | 730573 | 1892969 | 188245 | 1213937 | 3972109 | 0 | 46632 | 345722 | 34299 | 1228691 | 17511508 | 82.6112 | 71.1651 | 76.2804
| TMY15 WA | 8308162 | 692782 | 1892969 | 187331 | 1213937 | 4011100 | 0 | 44220 | 345722 | 34299 | 1228691 | 16730522 | 78.9269 | variance | variance
| XMY Min WA | 10880684 | 461897 | 1892969 | 183577 | 1213937 | 3771193 | 0 | 29483 | 345722 | 34299 | 1228691 | 18813761 | 88.7546 | 21.79% | 7.842%
| XMY Max WA | 6172578 | 926792 | 1892969 | 183202 | 1213937 | 4256559 | 0 | 59157 | 345722 | 34299 | 1228691 | 15085215 | 71.1651
4A - Baltimore | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 526262 | 2197995 | 1892969 | 182245 | 1213937 | 2134887 | 25878 | 140298 | 345722 | 34299 | 1228691 | 8694492 | 41.0166 | max EUI | max EUI
| TMY3 DOE | 526262 | 2230454 | 1892969 | 182689 | 1213937 | 2093357 | 24197 | 142369 | 345722 | 34299 | 1228691 | 8686255 | 40.9777 | 45.6066 | 42.6989
| TMY3 WA | 526262 | 2640792 | 1892969 | 190372 | 1213937 | 2019759 | 18419 | 168561 | 345722 | 34299 | 1228691 | 9051092 | 42.6989 | min EUI | min EUI
| TMY7 WA | 526262 | 2472063 | 1892969 | 191116 | 1213937 | 2058090 | 20988 | 157791 | 345722 | 34299 | 1228691 | 8913237 | 42.0485 | 39.3518 | 40.9777
| TMY15 WA | 526262 | 2605459 | 1892969 | 189302 | 1213937 | 2040727 | 19201 | 166306 | 345722 | 34299 | 1228691 | 9034184 | 42.6191 | variance | variance
| XMY Min WA | 526262 | 1585342 | 1892969 | 193519 | 1213937 | 2408055 | 40299 | 101192 | 345722 | 34299 | 1228691 | 8341596 | 39.3518 | 15.26% | 4.2%
| XMY Max WA | 526262 | 3404897 | 1892969 | 191273 | 1213937 | 1829990 | 10779 | 217334 | 345722 | 34299 | 1228691 | 9667462 | 45.6066
4B - Albuquerque | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 526262 | 1732059 | 1892969 | 177490 | 1213937 | 2144079 | 22577 | 110557 | 345722 | 34299 | 1228691 | 8199951 | 38.6836 | max EUI | max EUI
| TMY3 DOE | 526262 | 1716653 | 1892969 | 178747 | 1213937 | 2122280 | 21292 | 109574 | 345722 | 34299 | 1228691 | 8161735 | 38.5033 | 41.1534 | 40.1796
| TMY3 WA | 526262 | 2009062 | 1892969 | 180756 | 1213937 | 2160142 | 19687 | 128238 | 345722 | 34299 | 1228691 | 8511074 | 40.1513 | min EUI | min EUI
| TMY7 WA | 526262 | 1947784 | 1892969 | 181037 | 1213937 | 2225216 | 22622 | 124327 | 345722 | 34299 | 1228691 | 8514175 | 40.1659 | 38.5033 | 38.5033
| TMY15 WA | 526262 | 1976704 | 1892969 | 181043 | 1213937 | 2198116 | 21844 | 126173 | 345722 | 34299 | 1228691 | 8517069 | 40.1796 | variance | variance
| XMY Min WA | 526262 | 1451011 | 1892969 | 181150 | 1213937 | 2473101 | 38441 | 92618 | 345722 | 34299 | 1228691 | 8249510 | 38.9174 | 6.883% | 4.354%
| XMY Max WA | 526262 | 2320352 | 1892969 | 179748 | 1213937 | 2047165 | 14932 | 148108 | 345722 | 34299 | 1228691 | 8723494 | 41.1534
4C - Portland | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | #N/A | 1417172 | 2164525 | 184760 | 1203122 | 2088410 | 23527 | 90458 | 345722 | 34299 | 1228691 | #N/A | #N/A | max EUI | max EUI
| TMY3 DOE | #N/A | 1449538 | 2164525 | 186856 | 1203122 | 2055407 | 22510 | 92524 | 345722 | 34299 | 1228691 | #N/A | #N/A | #N/A | #N/A
| TMY3 WA | #N/A | 1625996 | 2164525 | 199050 | 1203122 | 2082249 | 21603 | 103787 | 345722 | 34299 | 1228691 | #N/A | #N/A | min EUI | min EUI
| TMY7 WA | #N/A | 1682356 | 2164525 | 195840 | 1203122 | 2203063 | 24317 | 107384 | 345722 | 34299 | 1228691 | #N/A | #N/A | #N/A | #N/A
| TMY15 WA | #N/A | 1667871 | 2164525 | 196879 | 1203122 | 2143942 | 22976 | 106460 | 345722 | 34299 | 1228691 | #N/A | #N/A | variance | variance
| XMY Min WA | #N/A | 1295286 | 2164525 | 194088 | 1203122 | 2627150 | 40373 | 82678 | 345722 | 34299 | 1228691 | #N/A | #N/A | #N/A | #N/A
| XMY Max WA | #N/A | 2084353 | 2164525 | 199563 | 1203122 | 1911674 | 15518 | 133044 | 345722 | 34299 | 1228691 | #N/A | #N/A
5A - Chicago | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 11913883 | 1948360 | 1892969 | 181694 | 1213937 | 2307585 | 35481 | 124363 | 345722 | 34299 | 1228691 | 19998293 | 94.3427 | max EUI | max EUI
| TMY3 DOE | 11650980 | 1997752 | 1892969 | 183540 | 1213937 | 2277909 | 34852 | 127516 | 345722 | 34299 | 1228691 | 19759476 | 93.2161 | 130.9934 | 94.3427
| TMY3 WA | 8334568 | 2175175 | 1892969 | 191961 | 1213937 | 2123757 | 26434 | 138841 | 345722 | 34299 | 1228691 | 16477663 | 77.734 | min EUI | min EUI
| TMY7 WA | 10185977 | 2083313 | 1892969 | 190991 | 1213937 | 2237702 | 31363 | 132977 | 345722 | 34299 | 1228691 | 18349250 | 86.5633 | 65.4894 | 77.734
| TMY15 WA | 9428094 | 2148199 | 1892969 | 190691 | 1213937 | 2198540 | 29090 | 137119 | 345722 | 34299 | 1228691 | 17618660 | 83.1167 | variance | variance
| XMY Min WA | 19872367 | 1459113 | 1892969 | 188582 | 1213937 | 2612176 | 55033 | 93135 | 345722 | 34299 | 1228691 | 27767333 | 130.9934 | 70.27% | 17.82%
| XMY Max WA | 5495478 | 2562398 | 1892969 | 193406 | 1213937 | 1962182 | 18171 | 163557 | 345722 | 34299 | 1228691 | 13882119 | 65.4894
5B - Boulder | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 8595412 | 1548799 | 2701816 | 179448 | 2023218 | 2187705 | 27353 | 98860 | 345722 | 34299 | 1228691 | 17742632 | 83.7015 | max EUI | max EUI
| TMY3 DOE | 8138570 | 1543085 | 2701816 | 181775 | 2023218 | 2174139 | 26237 | 98495 | 345722 | 34299 | 1228691 | 17267356 | 81.4594 | 144.3001 | 90.201
| TMY3 WA | 9725858 | 1530639 | 2701816 | 182708 | 2023218 | 2318332 | 31171 | 97700 | 345722 | 34299 | 1228691 | 18991463 | 89.5929 | min EUI | min EUI
| TMY7 WA | 9840633 | 1546757 | 2701816 | 182795 | 2023218 | 2315260 | 31118 | 98729 | 345722 | 34299 | 1228691 | 19120347 | 90.201 | 70.8555 | 81.4594
| TMY15 WA | 9444077 | 1555338 | 2701816 | 182320 | 2023218 | 2299216 | 30366 | 99277 | 345722 | 34299 | 1228691 | 18715649 | 88.2918 | variance | variance
| XMY Min WA | 21146785 | 1298317 | 2701816 | 185905 | 2023218 | 2710880 | 58207 | 82871 | 345722 | 34299 | 1228691 | 30588020 | 144.3001 | 90.16% | 10.73%
| XMY Max WA | 5678238 | 1810275 | 2701816 | 180405 | 2023218 | 2110278 | 19788 | 115549 | 345722 | 34299 | 1228691 | 15019588 | 70.8555
5C - Vancouver | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| doeCWEC | 8044943 | 1012550 | 2701816 | 198924 | 2023218 | 2039819 | 23952 | 64631 | 345722 | 34299 | 702429 | 16489874 | 77.7916 | max EUI | max EUI
| CWEC | 8045646 | 1008979 | 2701816 | 197873 | 2023218 | 2039912 | 23983 | 64403 | 345722 | 34299 | 702429 | 16485851 | 77.7726 | 105.8828 | 79.1109
| TMY3 WA | 6439652 | 1084989 | 2701816 | 198124 | 2023218 | 1924974 | 19783 | 69255 | 345722 | 34299 | 702429 | 14841832 | 70.0169 | min EUI | min EUI
| TMY7 WA | 8319537 | 986094 | 2701816 | 200013 | 2023218 | 2071131 | 24764 | 62942 | 345722 | 34299 | 702429 | 16769536 | 79.1109 | 63.7746 | 70.0169
| TMY15 WA | 7432676 | 1013762 | 2701816 | 199782 | 2023218 | 2000029 | 22648 | 64708 | 345722 | 34299 | 702429 | 15838660 | 74.7195 | variance | variance
| XMY Min WA | 13815131 | 866220 | 2701816 | 194764 | 2023218 | 2370803 | 37242 | 55291 | 345722 | 34299 | 702429 | 22444506 | 105.8828 | 54.14% | 11.69%
| XMY Max WA | 5115213 | 1178089 | 2701816 | 201408 | 2023218 | 1827053 | 16602 | 75197 | 345722 | 34299 | 702429 | 13518617 | 63.7746
6A - Minneapolis | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 13337164 | 1817923 | 2701816 | 182007 | 2023218 | 2263043 | 38281 | 116038 | 345722 | 34299 | 1228691 | 22859511 | 107.8406 | max EUI | max EUI
| TMY3 DOE | 12843576 | 1766402 | 2701816 | 184378 | 2023218 | 2253010 | 38018 | 112749 | 345722 | 34299 | 1228691 | 22303188 | 105.2161 | 150.6281 | 107.8406
| TMY3 WA | 8772608 | 2112429 | 2701816 | 192587 | 2023218 | 2115877 | 27472 | 134836 | 345722 | 34299 | 1228691 | 18460864 | 87.0898 | min EUI | min EUI
| TMY7 WA | 11952051 | 1930124 | 2701816 | 192030 | 2023218 | 2254135 | 35744 | 123199 | 345722 | 34299 | 1228691 | 21592338 | 101.8627 | 77.2861 | 87.0898
| TMY15 WA | 10216755 | 2035089 | 2701816 | 192430 | 2023218 | 2181311 | 30940 | 129899 | 345722 | 34299 | 1228691 | 19891479 | 93.8388 | variance | variance
| XMY Min WA | 22625518 | 1307622 | 2701816 | 191010 | 2023218 | 2555439 | 61280 | 83465 | 345722 | 34299 | 1228691 | 31929389 | 150.6281 | 69.71% | 19.72%
| XMY Max WA | 6024219 | 2793858 | 2701816 | 193137 | 2023218 | 2068417 | 19701 | 178331 | 345722 | 34299 | 1228691 | 16382718 | 77.2861
6B - Helena | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 12093262 | 1214541 | 2701816 | 181619 | 2023218 | 2211528 | 38118 | 77524 | 345722 | 34299 | 1228691 | 20921647 | 98.6987 | max EUI | max EUI
| TMY3 DOE | 11593479 | 1226360 | 2701816 | 183183 | 2023218 | 2215768 | 37164 | 78278 | 345722 | 34299 | 1228691 | 20439287 | 96.4231 | 161.1282 | 98.6987
| TMY3 WA | 10534030 | 1538387 | 2701816 | 187769 | 2023218 | 2287169 | 35095 | 98195 | 345722 | 34299 | 1228691 | 19785700 | 93.3398 | min EUI | min EUI
| TMY7 WA | 918637 | 6374902 | 2701816 | 184134 | 2023218 | 1945740 | 2384 | 406909 | 345722 | 34299 | 1228691 | 14937761 | 70.4694 | 70.4694 | 70.4694
| TMY15 WA | 11287146 | 1431173 | 2701816 | 187976 | 2023218 | 2297318 | 37056 | 91351 | 345722 | 34299 | 1228691 | 20437075 | 96.4127 | variance | variance
| XMY Min WA | 24850699 | 1144382 | 2701816 | 188683 | 2023218 | 2723822 | 69455 | 73046 | 345722 | 34299 | 1228691 | 34155142 | 161.1282 | 94.02% | 29.28%
| XMY Max WA | 7644854 | 1764943 | 2701816 | 185698 | 2023218 | 2124454 | 26616 | 112656 | 345722 | 34299 | 1228691 | 16964276 | 80.0296
7 - Duluth | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 16286989 | 1368783 | 2701816 | 181744 | 2023218 | 2414334 | 46862 | 87369 | 345722 | 34299 | 1228691 | 25491136 | 120.2554 | max EUI | max EUI
| TMY3 DOE | 15483600 | 1380401 | 2701816 | 184084 | 2023218 | 2381881 | 45196 | 88111 | 345722 | 34299 | 1228691 | 24668328 | 116.3738 | 158.2737 | 120.2554
| TMY3 WA | 10100956 | 1744915 | 2701816 | 195014 | 2023218 | 2211624 | 31831 | 111378 | 345722 | 34299 | 1228691 | 19500773 | 91.9956 | min EUI | min EUI
| TMY7 WA | 13022383 | 1638063 | 2701816 | 194789 | 2023218 | 2348249 | 39212 | 104557 | 345722 | 34299 | 1228691 | 22452308 | 105.9196 | 80.57 | 91.9956
| TMY15 WA | 11172005 | 1660417 | 2701816 | 193819 | 2023218 | 2250595 | 34447 | 105984 | 345722 | 34299 | 1228691 | 20522322 | 96.8148 | variance | variance
| XMY Min WA | 24235344 | 1208043 | 2701816 | 192124 | 2023218 | 2666822 | 65566 | 77109 | 345722 | 34299 | 1228691 | 33550063 | 158.2737 | 66.77% | 24.28%
| XMY Max WA | 7307783 | 2202738 | 2701816 | 197235 | 2023218 | 2101448 | 23967 | 140600 | 345722 | 34299 | 1228691 | 17078826 | 80.57
8 - Fairbanks | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 24755730 | 943896 | 2742519 | 202309 | 2023218 | 2556145 | 69136 | 60249 | 345722 | 34299 | 1228691 | 33733223 | 159.1377 | max EUI | max EUI
| TMY3 DOE | 22391785 | 963301 | 2742519 | 203529 | 2023218 | 2516242 | 64425 | 61487 | 345722 | 34299 | 1228691 | 31346527 | 147.8784 | 211.1911 | 159.1377
| TMY3 WA | 16517000 | 1161352 | 2742519 | 205713 | 2023218 | 2425071 | 51759 | 74129 | 345722 | 34299 | 1228691 | 25580782 | 120.6783 | min EUI | min EUI
| TMY7 WA | 20380107 | 1052578 | 2742519 | 205813 | 2023218 | 2527934 | 61402 | 67186 | 345722 | 34299 | 1228691 | 29440778 | 138.888 | 101.5961 | 120.6783
| TMY15 WA | 18759162 | 1111007 | 2742519 | 206163 | 2023218 | 2474358 | 56929 | 70915 | 345722 | 34299 | 1228691 | 27824292 | 131.2621 | variance | variance
| XMY Min WA | 35470914 | 910887 | 2742519 | 208685 | 2023218 | 2878958 | 93879 | 58142 | 345722 | 34299 | 1228691 | 44767223 | 211.1911 | 74.11% | 26.01%
| XMY Max WA | 12395496 | 1349946 | 2742519 | 205175 | 2023218 | 2311050 | 42232 | 86167 | 345722 | 34299 | 1228691 | 21535824 | 101.5961
1A - Miami
2A - Houston
2B - Phoenix
3A - Atlanta
3B - Las Vegas
3C - San Francisco
4A - Baltimore
4B - Albuquerque
4C - Portland
5A - Chicago
5B - Boulder
5C - Vancouver
6A - Minneapolis
6B - Helena
7 - Duluth
8 - Fairbanks

## 3s Additional Indicators
[14 empty] | Predicted Percentage Dissatisfied | [9 empty] | Peak Heating Load | [9 empty] | Peak Cooling Load
Climate Zone | Climate File | FLOOR 1 | Mech | FLOOR 2 | AUDITORIUM | GYM | KITCHEN CAFETERIA | Unmet Hours (Cooling) | UH Compliance | Peak Heating Load | Peak Cooling Load | EUI |  | Climate | [9 empty] | Climate | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | Climate | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY7WA | 84 | 25 | 91 | 24 | 18 | 0 | 2 | 2 | 3658993 | 1897464 | aaa |  | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 1A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3658993 | 12:00, January | 3658993 | 12:00, January | 3658993 | 1A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 22:30, May | 1897464 | 14:30, September | 696040
1A | TMY3WA | 89 | 29 | 94 | 28 | 20 | 0 | 1 | 1 | 3658993 | 1897464 | aaa | 1AFLOOR 1TMY7WA | 1A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 09:30,13/Feb | 99 | 16:30,10/Sep | 84 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY3 | 81 | 24 | 89 | 23 | 17 | 0 | 1 | 1 | 3658993 | 1897464 | aaa | 1AMECHTMY7WA | 1A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 02:30,15/Feb | 47 | 18:30,18/Jul | 25 | 2A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3817965 | 12:00, January | 3817965 | 12:00, January | 3817965 | 2A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1653078 | 14:30, September | 547931
1A | TMY2 | 80 | 23 | 89 | 22 | 16 | 0 | 0 | 0 | 3658993 | 1897464 | aaa | 1AFLOOR 2TMY7WA | 1A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 05:30,04/Jan | 100 | 14:30,20/Apr | 91 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY15WA | 86 | 27 | 92 | 26 | 19 | 0 | 0 | 0 | 3658993 | 1897464 | aaa | 1AAUDITORIUMTMY7WA | 1A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 07:30,11/Mar | 68 | 16:30,18/Jul | 24 | 2B | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3335691 | 12:00, January | 3335691 | 12:00, January | 3335691 | 2B | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 4526 | 02:30, May | 2398787 | 06:30, July | 966799
1A | MIN | 62 | 18 | 75 | 18 | 13 | 0 | 0 | 0 | 3658993 | 1897464 | aaa | 1AGYMTMY7WA | 1A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 08:30,28/Jan | 59 | 04:30,11/Sep | 18 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | MAX | 92 | 32 | 95 | 31 | 23 | 37 | 1 | 38 | 3658993 | 1897464 | aaa | 1AKITCHEN CAFETERIATMY7WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 11:30,02/Jan | 64 | 03:30,19/Aug | 24 | 3A | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4088501 | 12:00, January | 4088501 | 12:00, January | 4088501 | 3A | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1385332 | 16:30, September | 445901
2A | TMY7WA | 81 | 20 | 83 | 20 | 13 | 27 | 4 | 31 | 3817965 | 1653078 | aaa | 1AFLOOR 1TMY3WA | 1A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 27 | 07:30,23/Jan | 99 | 16:30,10/Sep | 89 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY3WA | 84 | 22 | 86 | 21 | 14 | 18 | 0 | 18 | 3817965 | 1653078 | aaa | 1AMECHTMY3WA | 1A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 03:30,23/Jan | 48 | 12:30,13/May | 29 | 3B | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3619627 | 12:00, January | 3619627 | 12:00, January | 3619627 | 3B | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 632 | 00:30, September | 2157150 | 06:30, July | 768158
2A | TMY3 | 77 | 19 | 80 | 19 | 13 | 1 | 4 | 5 | 3817965 | 1653078 | aaa | 1AFLOOR 2TMY3WA | 1A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 51 | 07:30,23/Jan | 100 | 15:30,22/Mar | 94 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY2 | 77 | 19 | 80 | 18 | 12 | 7 | 1 | 8 | 3817965 | 1653078 | aaa | 1AAUDITORIUMTMY3WA | 1A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 03:30,12/Feb | 68 | 14:30,25/Jul | 28 | 3C | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3224919 | 12:00, January | 3224919 | 12:00, January | 3224919 | 3C | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1134247 | 16:30, September | 233197
2A | TMY15WA | 83 | 20 | 84 | 20 | 13 | 7 | 1 | 8 | 3817965 | 1653078 | aaa | 1AGYMTMY3WA | 1A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 08:30,31/Mar | 59 | 04:30,11/Sep | 20 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | MIN | 58 | 19 | 63 | 17 | 12 | 0 | 20 | 20 | 3817965 | 1653078 | aaa | 1AKITCHEN CAFETERIATMY3WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 16:30,23/Jan | 64 | 05:30,09/Jul | 27 | 4A | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 4186155 | 12:00, January | 4186155 | 12:00, January | 4186155 | 4A | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 1398750 | 14:30, September | 455559
2A | MAX | 93 | 27 | 93 | 25 | 17 | 122 | 2 | 124 | 3817965 | 1653078 | aaa | 1AFLOOR 1TMY3 | 1A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 6 | 10:30,21/Mar | 99 | 15:30,22/Sep | 81 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY7WA | 80 | 20 | 81 | 18 | 15 | 18 | 9 | 27 | 3335691 | 2398787 | aaa | 1AMECHTMY3 | 1A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 04:30,25/Feb | 44 | 15:30,02/Sep | 24 | 4B | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 3979020 | 12:00, January | 3979020 | 12:00, January | 3979020 | 4B | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1620069 | 14:30, September | 492266
2B | TMY3WA | 82 | 22 | 83 | 20 | 16 | 5 | 15 | 20 | 3335691 | 2398787 | aaa | 1AFLOOR 2TMY3 | 1A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 22 | 05:30,04/Feb | 100 | 14:30,21/Jul | 89 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY3 | 83 | 22 | 84 | 21 | 17 | 7 | 16 | 23 | 3335691 | 2398787 | aaa | 1AAUDITORIUMTMY3 | 1A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 05:30,28/Jan | 67 | 13:30,02/Oct | 23 | 4C | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 3717432 | 12:00, January | 3717432 | 12:00, January | 3717432 | 4C | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 1320260 | 14:30, September | 420957
2B | TMY2 | 81 | 21 | 82 | 20 | 16 | 11 | 17 | 28 | 3335691 | 2398787 | aaa | 1AGYMTMY3 | 1A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,24/Feb | 60 | 03:30,18/Sep | 17 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY15WA | 80 | 21 | 81 | 19 | 16 | 11 | 21 | 32 | 3335691 | 2398787 | aaa | 1AKITCHEN CAFETERIATMY3 | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 12:30,24/Jan | 64 | 07:30,25/Jul | 23 | 5A | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 4783322 | 12:00, January | 4783322 | 12:00, January | 4783322 | 5A | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 1270638 | 14:30, September | 397236
2B | MIN | 64 | 19 | 67 | 16 | 12 | 0 | 28 | 28 | 3335691 | 2398787 | aaa | 1AFLOOR 1TMY2 | 1A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 18:30,02/Jan | 98 | 16:30,01/Sep | 80 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | MAX | 87 | 24 | 86 | 21 | 19 | 139 | 3 | 142 | 3335691 | 2398787 | aaa | 1AMECHTMY2 | 1A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 07:30,15/Feb | 41 | 13:30,06/Sep | 23 | 5B | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 4593127 | 12:00, January | 4593127 | 12:00, January | 4593127 | 5B | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 1229651 | 16:30, September | 297775
3A | TMY7WA | 69 | 18 | 72 | 16 | 11 | 47 | 2 | 49 | 4088501 | 1385332 | aaa | 1AFLOOR 2TMY2 | 1A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 8 | 11:30,03/Jan | 100 | 14:30,28/Jun | 89 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY3WA | 73 | 18 | 76 | 16 | 11 | 37 | 6 | 43 | 4088501 | 1385332 | aaa | 1AAUDITORIUMTMY2 | 1A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 09:30,11/Feb | 65 | 13:30,22/May | 22 | 5C | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 3827630 | 12:00, January | 3827630 | 12:00, January | 3827630 | 5C | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 727729 | 16:30, September | 149902
3A | TMY3 | 67 | 18 | 71 | 16 | 11 | 1 | 5 | 6 | 4088501 | 1385332 | aaa | 1AGYMTMY2 | 1A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,01/Feb | 59 | 05:30,18/Aug | 16 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY2 | 66 | 17 | 70 | 15 | 11 | 8 | 0 | 8 | 4088501 | 1385332 | aaa | 1AKITCHEN CAFETERIATMY2 | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 16:30,02/Jan | 63 | 07:30,12/Sep | 23 | 6A | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 5063981 | 12:00, January | 5063981 | 12:00, January | 5063981 | 6A | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 1230803 | 16:30, September | 400836
3A | TMY15WA | 71 | 18 | 74 | 16 | 11 | 3 | 6 | 9 | 4088501 | 1385332 | aaa | 1AFLOOR 1TMY15WA | 1A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 04:30,11/Jan | 99 | 16:30,07/Oct | 86 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | MIN | 49 | 20 | 54 | 15 | 11 | 0 | 11 | 11 | 4088501 | 1385332 | aaa | 1AMECHTMY15WA | 1A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 01:30,12/Jan | 48 | 14:30,20/Jul | 27 | 6B | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 5141729 | 12:00, January | 5141729 | 12:00, January | 5141729 | 6B | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 1160832 | 16:30, September | 277652
3A | MAX | 85 | 21 | 86 | 18 | 13 | 204 | 0 | 204 | 4088501 | 1385332 | aaa | 1AFLOOR 2TMY15WA | 1A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 20 | 07:30,09/Jan | 100 | 12:30,23/Apr | 92 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3B | TMY7WA | 73 | 19 | 75 | 17 | 14 | 22 | 19 | 41 | 3619627 | 2157150 | aaa | 1AAUDITORIUMTMY15WA | 1A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 22:30,27/Dec | 67 | 14:30,25/Jul | 26 | 7 | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 5145132 | 12:00, January | 5145132 | 12:00, January | 5145132 | 7 | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 962218 | 16:30, September | 252995
3B | TMY3WA | 74 | 20 | 76 | 18 | 14 | 4 | 18 | 22 | 3619627 | 2157150 | aaa | 1AGYMTMY15WA | 1A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,06/Mar | 59 | 04:30,09/Oct | 19 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3B | TMY3 | 73 | 20 | 76 | 18 | 15 | 8 | 19 | 27 | 3619627 | 2157150 | aaa | 1AKITCHEN CAFETERIATMY15WA | 1A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 15:30,09/Jan | 64 | 03:30,19/Aug | 26 | 8 | Heating plant sensible load | 46 rooms | RL_ILR.htg | Load (Btu/h) | 5939305 | 12:00, January | 5939305 | 12:00, January | 5939305 | 8 | Cooling plant sensible load | 46 rooms | RL_ILR.clg | Load (Btu/h) | 0 | 00:30, May | 855014 | 16:30, May | 186304
3B | TMY2 | 73 | 19 | 75 | 17 | 15 | 29 | 16 | 45 | 3619627 | 2157150 | aaa | 1AFLOOR 1MIN | 1A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 00:30,28/Mar | 98 | 15:30,01/Sep | 62
3B | TMY15WA | 73 | 19 | 74 | 17 | 14 | 17 | 20 | 37 | 3619627 | 2157150 | aaa | 1AMECHMIN | 1A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 03:30,06/Dec | 47 | 06:30,11/Jan | 18
3B | MIN | 55 | 20 | 60 | 15 | 12 | 0 | 29 | 29 | 3619627 | 2157150 | aaa | 1AFLOOR 2MIN | 1A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 14:30,14/Feb | 100 | 15:30,20/May | 75
3B | MAX | 81 | 20 | 82 | 19 | 16 | 463 | 1 | 464 | 3619627 | 2157150 | aaa | 1AAUDITORIUMMIN | 1A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 10:30,22/Nov | 66 | 12:30,20/Jun | 18
3C | TMY7WA | 56 | 7 | 62 | 8 | 7 | 33 | 2 | 35 | 3224919 | 1134247 | aaa | 1AGYMMIN | 1A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,07/Jan | 55 | 02:30,23/Aug | 13
3C | TMY3WA | 63 | 8 | 68 | 8 | 7 | 13 | 1 | 14 | 3224919 | 1134247 | aaa | 1AKITCHEN CAFETERIAMIN | 1A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 12:30,06/Feb | 64 | 06:30,22/Aug | 17
3C | TMY3 | 57 | 8 | 63 | 8 | 7 | 3 | 6 | 9 | 3224919 | 1134247 | aaa | 1AFLOOR 1MAX | 1A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 74 | 07:30,15/Jan | 99 | 16:30,01/Sep | 92
3C | TMY2 | 54 | 8 | 60 | 9 | 8 | 13 | 2 | 15 | 3224919 | 1134247 | aaa | 1AMECHMAX | 1A | People dissatisfied | MECH | MAX | Percentage (%) | 13 | 08:30,16/Jan | 50 | 14:30,03/Sep | 32
3C | TMY15WA | 58 | 8 | 64 | 8 | 7 | 7 | 2 | 9 | 3224919 | 1134247 | aaa | 1AFLOOR 2MAX | 1A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 82 | 01:30,18/Apr | 100 | 15:30,22/Mar | 95
3C | MIN | 44 | 11 | 51 | 10 | 8 | 0 | 33 | 33 | 3224919 | 1134247 | aaa | 1AAUDITORIUMMAX | 1A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 6 | 11:30,15/Jan | 68 | 13:30,25/Jul | 31
3C | MAX | 69 | 11 | 74 | 10 | 8 | 105 | 0 | 105 | 3224919 | 1134247 | aaa | 1AGYMMAX | 1A | People dissatisfied | GYM | MAX | Percentage (%) | 6 | 10:30,04/Dec | 60 | 03:30,11/Sep | 23
4A | TMY7WA_ILR | 15 | 20 | 16 | 16 | 11 | 108 | 67 | 175 | 4186155 | 1398750 | aaa | 1AKITCHEN CAFETERIAMAX | 1A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 6 | 08:30,15/Jan | 64 | 04:30,23/Oct | 29
4A | TMY3WA_ILR | 15 | 21 | 17 | 17 | 12 | 116 | 49 | 165 | 4186155 | 1398750 | aaa | 2ALocationFilename | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
4A | TMY3_ILR | 15 | 20 | 17 | 16 | 11 | 9 | 106 | 115 | 4186155 | 1398750 | aaa | 2AFLOOR 1TMY7WA | 2A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 8 | 05:30,19/Jan | 100 | 12:30,16/Aug | 81
4A | TMY2_ILR | 15 | 20 | 17 | 16 | 11 | 34 | 74 | 108 | 4186155 | 1398750 | aaa | 2AMECHTMY7WA | 2A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 23:30,05/Mar | 42 | 14:30,28/May | 20
4A | TMY15WA_ILR | 15 | 21 | 17 | 17 | 12 | 22 | 113 | 135 | 4186155 | 1398750 | aaa | 2AFLOOR 2TMY7WA | 2A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 8 | 17:30,17/Jan | 100 | 13:30,24/May | 83
4A | MIN_ILR | 15 | 20 | 16 | 16 | 11 | 0 | 115 | 115 | 4186155 | 1398750 | aaa | 2AAUDITORIUMTMY7WA | 2A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 16:30,09/Jan | 69 | 13:30,02/Oct | 20
4A | MAX_ILR | 18 | 25 | 20 | 19 | 13 | 478 | 34 | 512 | 4186155 | 1398750 | aaa | 2AGYMTMY7WA | 2A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 15:30,27/Feb | 54 | 00:30,16/Aug | 13
4B | TMY3_ILR | 14 | 19 | 15 | 15 | 14 | 116 | 946 | 1062 | 3979020 | 1620069 | aaa | 2AKITCHEN CAFETERIATMY7WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 16:30,06/Feb | 65 | 01:30,30/Aug | 20
4B | TMY2_ILR | 14 | 19 | 16 | 15 | 13 | 108 | 995 | 1103 | 3979020 | 1620069 | aaa | 2AFLOOR 1TMY3WA | 2A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 7 | 07:30,20/Dec | 100 | 16:30,28/Sep | 84
4B | TMY3WA_ILR | 13 | 19 | 15 | 14 | 14 | 80 | 1522 | 1602 | 3979020 | 1620069 | aaa | 2AMECHTMY3WA | 2A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 12:30,16/Dec | 48 | 14:30,20/Sep | 22
4B | TMY7WA_ILR | 13 | 19 | 15 | 14 | 13 | 125 | 1296 | 1421 | 3979020 | 1620069 | aaa | 2AFLOOR 2TMY3WA | 2A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 8 | 07:30,20/Dec | 100 | 15:30,21/May | 86
4B | TMY15WA_ILR | 13 | 19 | 15 | 14 | 14 | 106 | 1519 | 1625 | 3979020 | 1620069 | aaa | 2AAUDITORIUMTMY3WA | 2A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 09:30,16/Dec | 67 | 14:30,22/Aug | 21
4B | MIN_ILR | 15 | 20 | 16 | 16 | 12 | 22 | 2075 | 2097 | 3979020 | 1620069 | aaa | 2AGYMTMY3WA | 2A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 09:30,07/Feb | 54 | 00:30,16/Aug | 14
4B | MAX_ILR | 13 | 21 | 15 | 14 | 17 | 590 | 338 | 928 | 3979020 | 1620069 | aaa | 2AKITCHEN CAFETERIATMY3WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 10:30,20/Dec | 65 | 01:30,30/Aug | 22
4C | TMY3 ILR | 11 | 13 | 12 | 12 | 9 | 58 | 47 | 105 | 3717432 | 1320260 | aaa | 2AFLOOR 1TMY3 | 2A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 7 | 19:30,24/Jan | 99 | 15:30,03/Aug | 77
4C | TMY3WA ILR | 10 | 13 | 12 | 11 | 9 | 54 | 30 | 84 | 3717432 | 1320260 | aaa | 2AMECHTMY3 | 2A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 10:30,10/Dec | 40 | 07:30,23/Jan | 19
4C | TMY7WA ILR | 11 | 15 | 13 | 12 | 10 | 25 | 143 | 168 | 3717432 | 1320260 | aaa | 2AFLOOR 2TMY3 | 2A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 6 | 21:30,24/Jan | 100 | 13:30,02/Jul | 80
4C | TMY2 ILR | 11 | 13 | 12 | 12 | 9 | 66 | 166 | 232 | 3717432 | 1320260 | aaa | 2AAUDITORIUMTMY3 | 2A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 22:30,14/Jan | 67 | 09:30,29/Aug | 19
4C | MIN ILR | 15 | 21 | 15 | 16 | 11 | 37 | 175 | 212 | 3717432 | 1320260 | aaa | 2AGYMTMY3 | 2A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,07/Feb | 50 | 23:30,01/Aug | 13
4C | TMY15WA ILR | 11 | 14 | 13 | 12 | 9 | 0 | 675 | 675 | 3717432 | 1320260 | aaa | 2AKITCHEN CAFETERIATMY3 | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 19:30,04/Jan | 64 | 07:30,29/Aug | 19
4C | MAX ILR | 12 | 14 | 14 | 12 | 11 | 451 | 0 | 451 | 3717432 | 1320260 | aaa | 2AFLOOR 1TMY2 | 2A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 6 | 02:30,19/Jan | 99 | 16:30,16/Sep | 77
5A | MAX_ILR | 16 | 20 | 18 | 16 | 11 | 265 | 50 | 315 | 4783322 | 1270638 | aaa | 2AMECHTMY2 | 2A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 23:30,06/Nov | 48 | 06:30,14/Jan | 19
5A | MIN_ILR | 16 | 22 | 17 | 16 | 12 | 301 | 48 | 349 | 4783322 | 1270638 | aaa | 2AFLOOR 2TMY2 | 2A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 7 | 15:30,11/Dec | 100 | 15:30,26/May | 80
5A | TMY15WA_ILR | 15 | 19 | 16 | 16 | 11 | 57 | 42 | 99 | 4783322 | 1270638 | aaa | 2AAUDITORIUMTMY2 | 2A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 12:30,11/Feb | 66 | 11:30,17/Jul | 18
5A | TMY7WA_ILR | 15 | 19 | 16 | 16 | 11 | 173 | 26 | 199 | 4783322 | 1270638 | aaa | 2AGYMTMY2 | 2A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 09:30,06/Feb | 45 | 22:30,18/Jul | 12
5A | TMY3WA_ILR | 14 | 18 | 16 | 15 | 10 | 121 | 41 | 162 | 4783322 | 1270638 | aaa | 2AKITCHEN CAFETERIATMY2 | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 11:30,06/Feb | 65 | 07:30,18/Jul | 18
5A | TMY3_ILR | 15 | 19 | 16 | 16 | 11 | 6 | 97 | 103 | 4783322 | 1270638 | aaa | 2AFLOOR 1TMY15WA | 2A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 21 | 05:30,30/Dec | 100 | 12:30,16/Aug | 83
5A | TMY2_ILR | 15 | 19 | 16 | 16 | 11 | 839 | 0 | 839 | 4783322 | 1270638 | aaa | 2AMECHTMY15WA | 2A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 00:30,27/Jan | 42 | 13:30,23/Aug | 20
5B | TMY2_ILR | 13 | 18 | 15 | 15 | 13 | 244 | 1031 | 1275 | 4593127 | 1229651 | aaa | 2AFLOOR 2TMY15WA | 2A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 16 | 05:30,27/Dec | 100 | 15:30,21/May | 84
5B | TMY3_ILR | 13 | 18 | 15 | 14 | 13 | 212 | 1051 | 1263 | 4593127 | 1229651 | aaa | 2AAUDITORIUMTMY15WA | 2A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 04:30,24/Jan | 67 | 14:30,22/Aug | 20
5B | TMY3WA_ILR | 14 | 18 | 15 | 15 | 12 | 258 | 789 | 1047 | 4593127 | 1229651 | aaa | 2AGYMTMY15WA | 2A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 15:30,27/Feb | 54 | 00:30,16/Aug | 13
5B | TMY7WA_ILR | 14 | 18 | 15 | 15 | 12 | 312 | 810 | 1122 | 4593127 | 1229651 | aaa | 2AKITCHEN CAFETERIATMY15WA | 2A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 16:30,06/Feb | 65 | 02:30,30/Aug | 20
5B | TMY15WA_ILR | 14 | 18 | 15 | 15 | 12 | 255 | 864 | 1119 | 4593127 | 1229651 | aaa | 2AFLOOR 1MIN | 2A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 7 | 17:30,19/Jan | 99 | 16:30,29/Jul | 58
5B | MIN_ILR | 19 | 25 | 19 | 19 | 13 | 84 | 1651 | 1735 | 4593127 | 1229651 | aaa | 2AMECHMIN | 2A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 07:30,16/Oct | 53 | 07:30,10/Jan | 19
5B | MAX_ILR | 12 | 17 | 14 | 14 | 13 | 1415 | 77 | 1492 | 4593127 | 1229651 | aaa | 2AFLOOR 2MIN | 2A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 6 | 15:30,18/Dec | 100 | 14:30,13/Jul | 63
5C | doeCWEC_ILR | 11 | 14 | 12 | 12 | 9 | 51 | 10 | 61 | 3827630 | 727729 | aaa | 2AAUDITORIUMMIN | 2A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 12:30,24/Feb | 68 | 14:30,21/Aug | 17
5C | TMY3WA_ILR | 10 | 12 | 12 | 11 | 9 | 47 | 16 | 63 | 3827630 | 727729 | aaa | 2AGYMMIN | 2A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,11/Jan | 43 | 19:30,13/Jun | 12
5C | TMY7WA_ILR | 11 | 14 | 12 | 12 | 9 | 9 | 114 | 123 | 3827630 | 727729 | aaa | 2AKITCHEN CAFETERIAMIN | 2A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 12:30,28/Jan | 59 | 05:30,09/Aug | 15
5C | TMY15WA_ILR | 11 | 13 | 12 | 11 | 9 | 37 | 24 | 61 | 3827630 | 727729 | aaa | 2AFLOOR 1MAX | 2A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 68 | 00:30,18/Jan | 100 | 14:30,01/Sep | 93
5C | MAX_ILR | 10 | 12 | 12 | 11 | 9 | 20 | 25 | 45 | 3827630 | 727729 | aaa | 2AMECHMAX | 2A | People dissatisfied | MECH | MAX | Percentage (%) | 6 | 00:30,18/Jan | 54 | 15:30,03/Sep | 27
5C | MIN_ILR | 15 | 20 | 15 | 15 | 11 | 0 | 324 | 324 | 3827630 | 727729 | aaa | 2AFLOOR 2MAX | 2A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 64 | 00:30,18/Jan | 100 | 15:30,29/Mar | 93
5C | doeCWEC_ILR | 11 | 14 | 12 | 12 | 9 | 371 | 0 | 371 | 3827630 | 727729 | aaa | 2AAUDITORIUMMAX | 2A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 00:30,29/Dec | 67 | 13:30,08/Aug | 25
5C | CWEC_ILR | #N/A | #N/A | #N/A | #N/A | #N/A | 538 | 63 | 601 | 5063981 | 1230803 | aaa | 2AGYMMAX | 2A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 16:30,20/Feb | 58 | 04:30,03/Sep | 17
6A | TMY7WA | 15 | 20 | 17 | 16 | 11 | 429 | 120 | 549 | 5063981 | 1230803 | aaa | 2AKITCHEN CAFETERIAMAX | 2A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 6 | 09:30,16/Jan | 63 | 01:30,17/Aug | 25
6A | TMY3WA | 14 | 19 | 16 | 16 | 11 | 120 | 151 | 271 | 5063981 | 1230803 | aaa | 2BLocationFilename | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
6A | TMY3 | 16 | 21 | 17 | 17 | 12 | 375 | 140 | 515 | 5063981 | 1230803 | aaa | 2BFLOOR 1TMY7WA | 2B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 24 | 05:30,01/Jan | 100 | 16:30,10/Aug | 80
6A | TMY2 | 15 | 20 | 17 | 16 | 11 | 290 | 202 | 492 | 5063981 | 1230803 | aaa | 2BMECHTMY7WA | 2B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 07:30,13/Nov | 50 | 14:30,10/Aug | 20
6A | TMY15WA | 15 | 20 | 17 | 16 | 11 | 37 | 403 | 440 | 5063981 | 1230803 | aaa | 2BFLOOR 2TMY7WA | 2B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 21 | 06:30,27/Dec | 100 | 13:30,28/Jun | 81
6A | MIN | 17 | 23 | 18 | 18 | 12 | 1135 | 79 | 1214 | 5063981 | 1230803 | aaa | 2BAUDITORIUMTMY7WA | 2B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 04:30,21/Nov | 64 | 11:30,22/Aug | 18
6A | MAX | 17 | 23 | 19 | 17 | 13 | 423 | 675 | 1098 | 5141729 | 1160832 | aaa | 2BGYMTMY7WA | 2B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 21:30,11/Jan | 55 | 05:30,16/Aug | 15
6B | TMY7WA | 32 | 48 | 34 | 33 | 19 | 346 | 621 | 967 | 5141729 | 1160832 | aaa | 2BKITCHEN CAFETERIATMY7WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 20:30,20/Dec | 62 | 02:30,23/Aug | 18
6B | TMY3WA | 14 | 19 | 16 | 15 | 12 | 225 | 910 | 1135 | 5141729 | 1160832 | aaa | 2BFLOOR 1TMY3WA | 2B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 28 | 05:30,03/Dec | 100 | 15:30,26/Jul | 82
6B | TMY3 | 14 | 19 | 15 | 15 | 12 | 0 | 2140 | 2140 | 5141729 | 1160832 | aaa | 2BMECHTMY3WA | 2B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 00:30,30/Nov | 50 | 13:30,19/Jul | 22
6B | TMY2 | 14 | 19 | 16 | 15 | 12 | 253 | 771 | 1024 | 5141729 | 1160832 | aaa | 2BFLOOR 2TMY3WA | 2B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 25 | 05:30,02/Dec | 100 | 14:30,31/May | 83
6B | TMY15WA | 14 | 19 | 15 | 15 | 12 | 119 | 1475 | 1594 | 5141729 | 1160832 | aaa | 2BAUDITORIUMTMY3WA | 2B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 12:30,31/Dec | 63 | 14:30,22/Aug | 20
6B | MIN | 19 | 27 | 20 | 20 | 14 | 1341 | 72 | 1413 | 5141729 | 1160832 | aaa | 2BGYMTMY3WA | 2B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 15:30,31/Jan | 54 | 18:30,25/Jul | 16
6B | MAX | 13 | 18 | 15 | 14 | 14 | 720 | 44 | 764 | 5145132 | 962218 | aaa | 2BKITCHEN CAFETERIATMY3WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 19:30,31/Dec | 59 | 06:30,31/Jul | 20
7 | TMY7WA | 15 | 19 | 16 | 16 | 11 | 628 | 49 | 677 | 5145132 | 962218 | aaa | 2BFLOOR 1TMY3 | 2B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 32 | 05:30,11/Feb | 100 | 16:30,10/Aug | 83
7 | TMY3WA | 14 | 18 | 15 | 15 | 10 | 212 | 126 | 338 | 5145132 | 962218 | aaa | 2BMECHTMY3 | 2B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 08:30,09/Jan | 46 | 14:30,05/Jul | 22
7 | TMY3 | 15 | 20 | 16 | 16 | 11 | 429 | 93 | 522 | 5145132 | 962218 | aaa | 2BFLOOR 2TMY3 | 2B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 29 | 06:30,14/Dec | 100 | 13:30,15/Jun | 84
7 | TMY2 | 15 | 21 | 16 | 16 | 11 | 311 | 77 | 388 | 5145132 | 962218 | aaa | 2BAUDITORIUMTMY3 | 2B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 04:30,01/Apr | 65 | 12:30,18/Jul | 21
7 | TMY15WA | 14 | 18 | 16 | 15 | 11 | 59 | 242 | 301 | 5145132 | 962218 | aaa | 2BGYMTMY3 | 2B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 11:30,17/Jan | 56 | 18:30,08/Aug | 17
7 | MIN | 18 | 25 | 18 | 19 | 13 | 1241 | 19 | 1260 | 5145132 | 962218 | aaa | 2BKITCHEN CAFETERIATMY3 | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 13:30,23/Jan | 60 | 05:30,30/Jul | 20
7 | MAX | 15 | 20 | 17 | 16 | 11 | 1306 | 80 | 1386 | 5939305 | 855014 | aaa | 2BFLOOR 1TMY2 | 2B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 16 | 06:30,27/Dec | 100 | 16:30,16/Jul | 81
8 | TMY7WA | 16 | 22 | 17 | 17 | 12 | 1176 | 132 | 1308 | 5939305 | 855014 | aaa | 2BMECHTMY2 | 2B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 22:30,14/Feb | 45 | 12:30,27/Jun | 21
8 | TMY3WA | 15 | 21 | 17 | 16 | 12 | 699 | 441 | 1140 | 5939305 | 855014 | aaa | 2BFLOOR 2TMY2 | 2B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 15 | 06:30,27/Dec | 100 | 15:30,28/May | 82
8 | TMY3 | 17 | 23 | 18 | 18 | 12 | 977 | 246 | 1223 | 5939305 | 855014 | aaa | 2BAUDITORIUMTMY2 | 2B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 09:30,11/Feb | 64 | 15:30,18/Jul | 20
8 | TMY2 | 18 | 24 | 19 | 18 | 13 | 891 | 418 | 1309 | 5939305 | 855014 | aaa | 2BGYMTMY2 | 2B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,10/Mar | 55 | 18:30,11/Jul | 16
8 | TMY15WA | 16 | 22 | 18 | 17 | 12 | 224 | 955 | 1179 | 5939305 | 855014 | aaa | 2BKITCHEN CAFETERIATMY2 | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 18:30,19/Jan | 58 | 05:30,06/Aug | 19
8 | MIN | 22 | 30 | 22 | 23 | 15 | 1904 | 0 | 1904 | 5939305 | 855014 | aaa | 2BFLOOR 1TMY15WA | 2B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 25 | 06:30,28/Dec | 100 | 15:30,26/Jul | 80
8 | MAX | 15 | 21 | 17 | 16 | 13 | 1904 | 0 | 1904 | 5939305 | 855014 | aaa | 2BMECHTMY15WA | 2B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 04:30,25/Nov | 50 | 13:30,19/Jul | 21
[13 empty] | 2BFLOOR 2TMY15WA | 2B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 21 | 06:30,27/Dec | 100 | 14:30,28/May | 81
[13 empty] | 2BAUDITORIUMTMY15WA | 2B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 20:30,27/Dec | 62 | 14:30,01/Aug | 19
[13 empty] | 2BGYMTMY15WA | 2B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,18/Dec | 54 | 18:30,25/Jul | 16
[13 empty] | 2BKITCHEN CAFETERIATMY15WA | 2B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 17:30,07/Jan | 59 | 06:30,31/Jul | 19
[13 empty] | 2BFLOOR 1MIN | 2B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 8 | 07:30,04/Jan | 99 | 12:30,07/Sep | 64
[13 empty] | 2BMECHMIN | 2B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 01:30,20/Apr | 41 | 14:30,06/Sep | 19
[13 empty] | 2BFLOOR 2MIN | 2B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 9 | 06:30,05/Jan | 100 | 14:30,06/Sep | 67
[13 empty] | 2BAUDITORIUMMIN | 2B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 09:30,05/Mar | 60 | 15:30,11/Jul | 16
[13 empty] | 2BGYMMIN | 2B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 10:30,18/Jan | 47 | 05:30,20/Jul | 12
[13 empty] | 2BKITCHEN CAFETERIAMIN | 2B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 20:30,28/Jan | 58 | 04:30,08/Sep | 14
[13 empty] | 2BFLOOR 1MAX | 2B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 51 | 05:30,01/Jan | 100 | 16:30,23/Jul | 87
[13 empty] | 2BMECHMAX | 2B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 01:30,03/Jan | 49 | 13:30,06/Sep | 24
[13 empty] | 2BFLOOR 2MAX | 2B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 51 | 07:30,26/Dec | 100 | 14:30,11/May | 86
[13 empty] | 2BAUDITORIUMMAX | 2B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 02:30,27/Jan | 62 | 13:30,11/Jul | 21
[13 empty] | 2BGYMMAX | 2B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 08:30,29/Dec | 56 | 19:30,25/Jul | 19
[13 empty] | 2BKITCHEN CAFETERIAMAX | 2B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 08:30,30/Dec | 56 | 18:30,25/Jul | 22
[13 empty] | 3ALocationFilename | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 3AFLOOR 1TMY7WA | 3A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 7 | 20:30,15/Feb | 99 | 16:30,12/Jul | 69
[13 empty] | 3AMECHTMY7WA | 3A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 21:30,30/Oct | 42 | 14:30,01/Aug | 18
[13 empty] | 3AFLOOR 2TMY7WA | 3A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 7 | 16:30,14/Feb | 100 | 13:30,07/Jul | 72
[13 empty] | 3AAUDITORIUMTMY7WA | 3A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 10:30,27/Nov | 65 | 12:30,14/Aug | 16
[13 empty] | 3AGYMTMY7WA | 3A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 13:30,17/Jan | 46 | 03:30,26/Jul | 11
[13 empty] | 3AKITCHEN CAFETERIATMY7WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 18:30,05/Jan | 63 | 07:30,25/Jul | 15
[13 empty] | 3AFLOOR 1TMY3WA | 3A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 7 | 04:30,01/Mar | 99 | 16:30,26/Jul | 73
[13 empty] | 3AMECHTMY3WA | 3A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 23:30,15/Oct | 41 | 14:30,01/Aug | 18
[13 empty] | 3AFLOOR 2TMY3WA | 3A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 10 | 05:30,25/Feb | 100 | 16:30,14/May | 76
[13 empty] | 3AAUDITORIUMTMY3WA | 3A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 04:30,04/May | 65 | 12:30,14/Aug | 16
[13 empty] | 3AGYMTMY3WA | 3A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 13:30,16/Jan | 45 | 19:30,27/Jun | 11
[13 empty] | 3AKITCHEN CAFETERIATMY3WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 12:30,03/Jan | 62 | 02:30,19/Jul | 16
[13 empty] | 3AFLOOR 1TMY3 | 3A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 7 | 05:30,07/Dec | 99 | 16:30,08/Jul | 67
[13 empty] | 3AMECHTMY3 | 3A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 08:30,28/Apr | 37 | 20:30,13/Feb | 18
[13 empty] | 3AFLOOR 2TMY3 | 3A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 7 | 17:30,05/Dec | 100 | 13:30,18/Aug | 71
[13 empty] | 3AAUDITORIUMTMY3 | 3A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 14:30,18/Mar | 63 | 13:30,22/Aug | 16
[13 empty] | 3AGYMTMY3 | 3A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 15:30,31/Oct | 39 | 19:30,01/Aug | 11
[13 empty] | 3AKITCHEN CAFETERIATMY3 | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 16:30,13/Nov | 56 | 04:30,09/Aug | 16
[13 empty] | 3AFLOOR 1TMY2 | 3A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 7 | 05:30,17/Feb | 98 | 16:30,03/Jul | 66
[13 empty] | 3AMECHTMY2 | 3A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 03:30,16/Oct | 41 | 06:30,10/Feb | 17
[13 empty] | 3AFLOOR 2TMY2 | 3A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 7 | 17:30,03/Jan | 100 | 12:30,26/Jul | 70
[13 empty] | 3AAUDITORIUMTMY2 | 3A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 10:30,29/Dec | 64 | 16:30,31/Jul | 15
[13 empty] | 3AGYMTMY2 | 3A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 14:30,28/Nov | 41 | 21:30,03/Jul | 11
[13 empty] | 3AKITCHEN CAFETERIATMY2 | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 14:30,01/Feb | 57 | 07:30,04/Jul | 15
[13 empty] | 3AFLOOR 1TMY15WA | 3A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 7 | 18:30,08/Feb | 99 | 16:30,12/Jul | 71
[13 empty] | 3AMECHTMY15WA | 3A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 01:30,28/Oct | 42 | 14:30,01/Aug | 18
[13 empty] | 3AFLOOR 2TMY15WA | 3A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 8 | 16:30,06/Feb | 100 | 13:30,07/Jul | 74
[13 empty] | 3AAUDITORIUMTMY15WA | 3A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 15:30,04/Mar | 65 | 12:30,14/Aug | 16
[13 empty] | 3AGYMTMY15WA | 3A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 13:30,16/Jan | 46 | 03:30,26/Jul | 11
[13 empty] | 3AKITCHEN CAFETERIATMY15WA | 3A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 12:30,03/Jan | 63 | 07:30,25/Jul | 16
[13 empty] | 3AFLOOR 1MIN | 3A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 7 | 17:30,29/Mar | 96 | 16:30,09/Aug | 49
[13 empty] | 3AMECHMIN | 3A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 00:30,30/Sep | 51 | 08:30,24/Jan | 20
[13 empty] | 3AFLOOR 2MIN | 3A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 6 | 18:30,27/Mar | 99 | 15:30,28/Jul | 54
[13 empty] | 3AAUDITORIUMMIN | 3A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 16:30,24/Nov | 51 | 17:30,24/Jul | 15
[13 empty] | 3AGYMMIN | 3A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 13:30,01/Dec | 46 | 07:30,24/Jan | 11
[13 empty] | 3AKITCHEN CAFETERIAMIN | 3A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 15:30,16/Feb | 43 | 00:30,12/Jul | 13
[13 empty] | 3AFLOOR 1MAX | 3A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 35 | 04:30,27/Dec | 100 | 15:30,30/Jun | 85
[13 empty] | 3AMECHMAX | 3A | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 09:30,21/Feb | 44 | 15:30,18/Jul | 21
[13 empty] | 3AFLOOR 2MAX | 3A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 29 | 07:30,07/Feb | 100 | 16:30,21/May | 86
[13 empty] | 3AAUDITORIUMMAX | 3A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 22:30,22/Jan | 65 | 16:30,01/Aug | 18
[13 empty] | 3AGYMMAX | 3A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 12:30,07/Feb | 54 | 20:30,18/Jul | 13
[13 empty] | 3AKITCHEN CAFETERIAMAX | 3A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 15:30,25/Dec | 60 | 07:30,25/Jul | 20
[13 empty] | 3BLocationFilename | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 3BFLOOR 1TMY7WA | 3B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 9 | 04:30,01/Jan | 99 | 14:30,17/Sep | 73
[13 empty] | 3BMECHTMY7WA | 3B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 01:30,04/Apr | 44 | 14:30,08/Jul | 19
[13 empty] | 3BFLOOR 2TMY7WA | 3B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 12 | 05:30,06/Jan | 100 | 13:30,06/Jul | 75
[13 empty] | 3BAUDITORIUMTMY7WA | 3B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 00:30,01/Nov | 57 | 10:30,11/Jul | 17
[13 empty] | 3BGYMTMY7WA | 3B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 10:30,30/Dec | 51 | 01:30,26/Jul | 14
[13 empty] | 3BKITCHEN CAFETERIATMY7WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 14:30,28/Nov | 55 | 05:30,08/Sep | 16
[13 empty] | 3BFLOOR 1TMY3WA | 3B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 14 | 04:30,06/Dec | 99 | 15:30,12/Aug | 74
[13 empty] | 3BMECHTMY3WA | 3B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 21:30,05/Nov | 45 | 14:30,12/Aug | 20
[13 empty] | 3BFLOOR 2TMY3WA | 3B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 19 | 05:30,24/Dec | 100 | 13:30,06/Jul | 76
[13 empty] | 3BAUDITORIUMTMY3WA | 3B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 11:30,28/Feb | 57 | 14:30,01/Aug | 18
[13 empty] | 3BGYMTMY3WA | 3B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 12:30,24/Jan | 52 | 02:30,13/Aug | 14
[13 empty] | 3BKITCHEN CAFETERIATMY3WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 14:30,28/Nov | 57 | 07:30,22/Aug | 17
[13 empty] | 3BFLOOR 1TMY3 | 3B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 17 | 05:30,16/Feb | 100 | 15:30,05/Jul | 73
[13 empty] | 3BMECHTMY3 | 3B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 05:30,01/Mar | 43 | 14:30,01/Sep | 20
[13 empty] | 3BFLOOR 2TMY3 | 3B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 14 | 05:30,16/Feb | 100 | 14:30,05/Jul | 76
[13 empty] | 3BAUDITORIUMTMY3 | 3B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 11:30,19/Mar | 60 | 13:30,07/Aug | 18
[13 empty] | 3BGYMTMY3 | 3B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 10:30,13/Feb | 53 | 20:30,08/Aug | 15
[13 empty] | 3BKITCHEN CAFETERIATMY3 | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 20:30,09/Feb | 58 | 02:30,22/Jun | 17
[13 empty] | 3BFLOOR 1TMY2 | 3B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 10 | 06:30,11/Jan | 99 | 14:30,05/Aug | 73
[13 empty] | 3BMECHTMY2 | 3B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 00:30,25/Mar | 45 | 14:30,26/Jul | 19
[13 empty] | 3BFLOOR 2TMY2 | 3B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 9 | 06:30,11/Jan | 100 | 13:30,26/Jul | 75
[13 empty] | 3BAUDITORIUMTMY2 | 3B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 14:30,22/Dec | 60 | 13:30,07/Aug | 17
[13 empty] | 3BGYMTMY2 | 3B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 21:30,03/Feb | 53 | 07:30,11/Jul | 15
[13 empty] | 3BKITCHEN CAFETERIATMY2 | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 17:30,16/Jan | 54 | 03:30,06/Aug | 16
[13 empty] | 3BFLOOR 1TMY15WA | 3B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 13 | 04:30,06/Jan | 99 | 12:30,14/Jul | 73
[13 empty] | 3BMECHTMY15WA | 3B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 07:30,04/Apr | 44 | 14:30,08/Jul | 19
[13 empty] | 3BFLOOR 2TMY15WA | 3B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 13 | 05:30,05/Jan | 100 | 13:30,06/Jul | 74
[13 empty] | 3BAUDITORIUMTMY15WA | 3B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 11:30,20/Jan | 57 | 10:30,11/Jul | 17
[13 empty] | 3BGYMTMY15WA | 3B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,06/Mar | 51 | 03:30,14/Jul | 14
[13 empty] | 3BKITCHEN CAFETERIATMY15WA | 3B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 14:30,28/Nov | 57 | 23:30,01/Aug | 16
[13 empty] | 3BFLOOR 1MIN | 3B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 8 | 17:30,01/Feb | 97 | 16:30,27/Jul | 55
[13 empty] | 3BMECHMIN | 3B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 07:30,06/May | 49 | 06:30,15/Jan | 20
[13 empty] | 3BFLOOR 2MIN | 3B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 7 | 16:30,09/Jan | 99 | 14:30,10/Aug | 60
[13 empty] | 3BAUDITORIUMMIN | 3B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 18:30,15/Feb | 56 | 11:30,24/Jul | 15
[13 empty] | 3BGYMMIN | 3B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 12:30,15/Dec | 39 | 05:30,30/Jul | 12
[13 empty] | 3BKITCHEN CAFETERIAMIN | 3B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 20:30,10/Nov | 52 | 05:30,30/Jul | 13
[13 empty] | 3BFLOOR 1MAX | 3B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 35 | 04:30,04/Jan | 99 | 16:30,01/Sep | 81
[13 empty] | 3BMECHMAX | 3B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 01:30,02/Dec | 47 | 14:30,17/Jul | 20
[13 empty] | 3BFLOOR 2MAX | 3B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 32 | 05:30,29/Dec | 100 | 14:30,19/May | 82
[13 empty] | 3BAUDITORIUMMAX | 3B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 02:30,09/Mar | 58 | 13:30,05/Sep | 19
[13 empty] | 3BGYMMAX | 3B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 12:30,19/Dec | 53 | 02:30,27/Jul | 16
[13 empty] | 3BKITCHEN CAFETERIAMAX | 3B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 10:30,16/Jan | 53 | 00:30,27/Jul | 19
[13 empty] | 3CLocationFilename | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 3CFLOOR 1TMY7WA | 3C | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 22 | 05:30,11/Jan | 88 | 14:30,14/Oct | 56
[13 empty] | 3CMECHTMY7WA | 3C | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 02:30,01/Sep | 31 | 06:30,11/Jan | 7
[13 empty] | 3CFLOOR 2TMY7WA | 3C | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 23 | 07:30,10/Jan | 98 | 14:30,14/Oct | 62
[13 empty] | 3CAUDITORIUMTMY7WA | 3C | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 09:30,12/Jan | 26 | 03:30,11/Jan | 8
[13 empty] | 3CGYMTMY7WA | 3C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 13:30,21/Mar | 27 | 07:30,10/Jan | 7
[13 empty] | 3CKITCHEN CAFETERIATMY7WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 20:30,11/Jan | 25 | 10:30,14/Oct | 8
[13 empty] | 3CFLOOR 1TMY3WA | 3C | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 25 | 05:30,09/Feb | 92 | 14:30,05/Oct | 63
[13 empty] | 3CMECHTMY3WA | 3C | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 23:30,30/Jul | 27 | 14:30,05/Oct | 8
[13 empty] | 3CFLOOR 2TMY3WA | 3C | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 23 | 05:30,09/Feb | 98 | 14:30,23/Sep | 68
[13 empty] | 3CAUDITORIUMTMY3WA | 3C | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 14:30,30/Mar | 31 | 15:30,03/Oct | 8
[13 empty] | 3CGYMTMY3WA | 3C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 09:30,25/Dec | 22 | 05:30,08/Feb | 7
[13 empty] | 3CKITCHEN CAFETERIATMY3WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 19:30,30/Dec | 29 | 06:30,25/Sep | 10
[13 empty] | 3CFLOOR 1TMY3 | 3C | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 24 | 05:30,11/Jan | 89 | 14:30,24/Sep | 57
[13 empty] | 3CMECHTMY3 | 3C | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 23:30,22/May | 31 | 06:30,11/Jan | 8
[13 empty] | 3CFLOOR 2TMY3 | 3C | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 23 | 07:30,26/Dec | 98 | 15:30,15/Sep | 63
[13 empty] | 3CAUDITORIUMTMY3 | 3C | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 04:30,27/Sep | 25 | 05:30,27/Dec | 8
[13 empty] | 3CGYMTMY3 | 3C | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 09:30,18/Dec | 26 | 05:30,27/Dec | 7
[13 empty] | 3CKITCHEN CAFETERIATMY3 | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 12:30,25/Dec | 23 | 10:30,12/May | 8
[13 empty] | 3CFLOOR 1TMY2 | 3C | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 22 | 05:30,26/Dec | 92 | 14:30,30/Sep | 54
[13 empty] | 3CMECHTMY2 | 3C | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 00:30,13/Sep | 34 | 07:30,26/Dec | 8
[13 empty] | 3CFLOOR 2TMY2 | 3C | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 21 | 07:30,02/Jan | 98 | 16:30,28/Sep | 60
[13 empty] | 3CAUDITORIUMTMY2 | 3C | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 08:30,23/Mar | 36 | 14:30,03/Jul | 9
[13 empty] | 3CGYMTMY2 | 3C | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 13:30,20/Mar | 29 | 05:30,26/Dec | 8
[13 empty] | 3CKITCHEN CAFETERIATMY2 | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 09:30,10/Apr | 29 | 04:30,30/Sep | 8
[13 empty] | 3CFLOOR 1TMY15WA | 3C | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 28 | 07:30,25/Dec | 92 | 14:30,20/Sep | 58
[13 empty] | 3CMECHTMY15WA | 3C | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 01:30,10/Oct | 27 | 14:30,20/Sep | 8
[13 empty] | 3CFLOOR 2TMY15WA | 3C | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 28 | 05:30,20/Jan | 98 | 14:30,17/Sep | 64
[13 empty] | 3CAUDITORIUMTMY15WA | 3C | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 11:30,10/Mar | 41 | 14:30,19/Sep | 8
[13 empty] | 3CGYMTMY15WA | 3C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 15:30,17/Jan | 18 | 17:30,31/May | 7
[13 empty] | 3CKITCHEN CAFETERIATMY15WA | 3C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 08:30,06/Dec | 29 | 19:30,19/Sep | 9
[13 empty] | 3CFLOOR 1MIN | 3C | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 20 | 05:30,13/Jan | 79 | 14:30,10/Sep | 44
[13 empty] | 3CMECHMIN | 3C | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 02:30,11/Sep | 37 | 04:30,13/Jan | 11
[13 empty] | 3CFLOOR 2MIN | 3C | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 20 | 05:30,13/Jan | 94 | 15:30,10/Sep | 51
[13 empty] | 3CAUDITORIUMMIN | 3C | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 14:30,15/Mar | 28 | 03:30,06/Dec | 10
[13 empty] | 3CGYMMIN | 3C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 13:30,12/Jun | 30 | 02:30,06/Dec | 8
[13 empty] | 3CKITCHEN CAFETERIAMIN | 3C | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 17:30,27/Jan | 19 | 13:30,09/Sep | 7
[13 empty] | 3CFLOOR 1MAX | 3C | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 39 | 23:30,03/Jan | 93 | 14:30,30/Sep | 69
[13 empty] | 3CMECHMAX | 3C | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 21:30,04/Dec | 30 | 14:30,13/Sep | 11
[13 empty] | 3CFLOOR 2MAX | 3C | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 38 | 00:30,04/Jan | 99 | 14:30,13/Sep | 74
[13 empty] | 3CAUDITORIUMMAX | 3C | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 07:30,18/Mar | 47 | 15:30,29/Aug | 10
[13 empty] | 3CGYMMAX | 3C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 15:30,14/Feb | 22 | 17:30,26/Oct | 8
[13 empty] | 3CKITCHEN CAFETERIAMAX | 3C | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 08:30,20/Jan | 36 | 19:30,29/Aug | 12
[13 empty] | 4ALocationFilename | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 4AFLOOR 1TMY7WA_ILR | 4A | People dissatisfied | FLOOR 1 | TMY7WA_ILR | Percentage (%) | 5 | 07:30,05/Oct | 58 | 09:30,25/Jul | 15
[13 empty] | 4AMECHTMY7WA_ILR | 4A | People dissatisfied | MECH | TMY7WA_ILR | Percentage (%) | 5 | 03:30,17/Apr | 67 | 13:30,25/Jul | 20
[13 empty] | 4AFLOOR 2TMY7WA_ILR | 4A | People dissatisfied | FLOOR 2 | TMY7WA_ILR | Percentage (%) | 5 | 07:30,19/Oct | 58 | 11:30,25/Jul | 16
[13 empty] | 4AAUDITORIUMTMY7WA_ILR | 4A | People dissatisfied | AUDITORIUM | TMY7WA_ILR | Percentage (%) | 5 | 10:30,05/Feb | 63 | 10:30,25/Jul | 16
[13 empty] | 4AGYMTMY7WA_ILR | 4A | People dissatisfied | GYM | TMY7WA_ILR | Percentage (%) | 5 | 08:30,31/Dec | 39 | 07:30,24/Jul | 11
[13 empty] | 4AKITCHEN CAFETERIATMY7WA_ILR | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA_ILR | Percentage (%) | 5 | 19:30,01/Dec | 56 | 07:30,25/Jul | 14
[13 empty] | 4AFLOOR 1TMY3WA_ILR | 4A | People dissatisfied | FLOOR 1 | TMY3WA_ILR | Percentage (%) | 5 | 07:30,23/Apr | 58 | 09:30,25/Jul | 15
[13 empty] | 4AMECHTMY3WA_ILR | 4A | People dissatisfied | MECH | TMY3WA_ILR | Percentage (%) | 5 | 22:30,03/Nov | 68 | 13:30,25/Jul | 21
[13 empty] | 4AFLOOR 2TMY3WA_ILR | 4A | People dissatisfied | FLOOR 2 | TMY3WA_ILR | Percentage (%) | 5 | 06:30,30/Sep | 58 | 11:30,25/Jul | 17
[13 empty] | 4AAUDITORIUMTMY3WA_ILR | 4A | People dissatisfied | AUDITORIUM | TMY3WA_ILR | Percentage (%) | 5 | 19:30,15/Jan | 64 | 10:30,25/Jul | 17
[13 empty] | 4AGYMTMY3WA_ILR | 4A | People dissatisfied | GYM | TMY3WA_ILR | Percentage (%) | 5 | 14:30,27/Nov | 39 | 07:30,24/Jul | 12
[13 empty] | 4AKITCHEN CAFETERIATMY3WA_ILR | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA_ILR | Percentage (%) | 5 | 20:30,12/Feb | 56 | 07:30,25/Jul | 15
[13 empty] | 4AFLOOR 1TMY3_ILR | 4A | People dissatisfied | FLOOR 1 | TMY3_ILR | Percentage (%) | 5 | 07:30,23/Apr | 50 | 12:30,10/Jul | 15
[13 empty] | 4AMECHTMY3_ILR | 4A | People dissatisfied | MECH | TMY3_ILR | Percentage (%) | 5 | 09:30,13/Apr | 53 | 15:30,09/Jul | 20
[13 empty] | 4AFLOOR 2TMY3_ILR | 4A | People dissatisfied | FLOOR 2 | TMY3_ILR | Percentage (%) | 5 | 07:30,22/Oct | 57 | 12:30,05/Sep | 17
[13 empty] | 4AAUDITORIUMTMY3_ILR | 4A | People dissatisfied | AUDITORIUM | TMY3_ILR | Percentage (%) | 5 | 09:30,01/Feb | 63 | 16:30,14/Aug | 16
[13 empty] | 4AGYMTMY3_ILR | 4A | People dissatisfied | GYM | TMY3_ILR | Percentage (%) | 5 | 14:30,11/Jan | 46 | 07:30,26/Dec | 11
[13 empty] | 4AKITCHEN CAFETERIATMY3_ILR | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY3_ILR | Percentage (%) | 5 | 13:30,07/Nov | 52 | 07:30,11/Jul | 14
[13 empty] | 4AFLOOR 1TMY2_ILR | 4A | People dissatisfied | FLOOR 1 | TMY2_ILR | Percentage (%) | 5 | 07:30,28/Apr | 53 | 12:30,25/Jul | 15
[13 empty] | 4AMECHTMY2_ILR | 4A | People dissatisfied | MECH | TMY2_ILR | Percentage (%) | 5 | 20:30,08/May | 54 | 13:30,25/Jul | 20
[13 empty] | 4AFLOOR 2TMY2_ILR | 4A | People dissatisfied | FLOOR 2 | TMY2_ILR | Percentage (%) | 5 | 07:30,15/Oct | 59 | 10:30,25/Jul | 17
[13 empty] | 4AAUDITORIUMTMY2_ILR | 4A | People dissatisfied | AUDITORIUM | TMY2_ILR | Percentage (%) | 5 | 14:30,03/Mar | 69 | 11:30,25/Jul | 16
[13 empty] | 4AGYMTMY2_ILR | 4A | People dissatisfied | GYM | TMY2_ILR | Percentage (%) | 5 | 14:30,21/Jan | 46 | 05:30,18/Jan | 11
[13 empty] | 4AKITCHEN CAFETERIATMY2_ILR | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY2_ILR | Percentage (%) | 5 | 19:30,26/Feb | 55 | 07:30,25/Jul | 14
[13 empty] | 4AFLOOR 1TMY15WA_ILR | 4A | People dissatisfied | FLOOR 1 | TMY15WA_ILR | Percentage (%) | 5 | 07:30,23/Apr | 58 | 09:30,25/Jul | 15
[13 empty] | 4AMECHTMY15WA_ILR | 4A | People dissatisfied | MECH | TMY15WA_ILR | Percentage (%) | 5 | 22:30,03/Nov | 67 | 13:30,25/Jul | 21
[13 empty] | 4AFLOOR 2TMY15WA_ILR | 4A | People dissatisfied | FLOOR 2 | TMY15WA_ILR | Percentage (%) | 5 | 07:30,14/Oct | 58 | 11:30,25/Jul | 17
[13 empty] | 4AAUDITORIUMTMY15WA_ILR | 4A | People dissatisfied | AUDITORIUM | TMY15WA_ILR | Percentage (%) | 5 | 17:30,03/Apr | 63 | 10:30,25/Jul | 17
[13 empty] | 4AGYMTMY15WA_ILR | 4A | People dissatisfied | GYM | TMY15WA_ILR | Percentage (%) | 5 | 14:30,27/Nov | 39 | 07:30,24/Jul | 12
[13 empty] | 4AKITCHEN CAFETERIATMY15WA_ILR | 4A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA_ILR | Percentage (%) | 5 | 17:30,02/Feb | 56 | 07:30,25/Jul | 15
[13 empty] | 4AFLOOR 1MIN_ILR | 4A | People dissatisfied | FLOOR 1 | MIN_ILR | Percentage (%) | 5 | 07:30,24/Sep | 40 | 04:30,25/Jan | 15
[13 empty] | 4AMECHMIN_ILR | 4A | People dissatisfied | MECH | MIN_ILR | Percentage (%) | 5 | 09:30,22/Sep | 47 | 07:30,24/Jan | 20
[13 empty] | 4AFLOOR 2MIN_ILR | 4A | People dissatisfied | FLOOR 2 | MIN_ILR | Percentage (%) | 5 | 07:30,24/Sep | 49 | 17:30,01/Aug | 16
[13 empty] | 4AAUDITORIUMMIN_ILR | 4A | People dissatisfied | AUDITORIUM | MIN_ILR | Percentage (%) | 5 | 20:30,19/Nov | 44 | 10:30,17/Jan | 16
[13 empty] | 4AGYMMIN_ILR | 4A | People dissatisfied | GYM | MIN_ILR | Percentage (%) | 5 | 00:30,08/Jun | 46 | 07:30,17/Jan | 11
[13 empty] | 4AKITCHEN CAFETERIAMIN_ILR | 4A | People dissatisfied | KITCHEN CAFETERIA | MIN_ILR | Percentage (%) | 5 | 15:30,19/Nov | 40 | 22:30,17/Jan | 13
[13 empty] | 4AFLOOR 1MAX_ILR | 4A | People dissatisfied | FLOOR 1 | MAX_ILR | Percentage (%) | 5 | 07:30,31/Mar | 58 | 04:30,02/Aug | 18
[13 empty] | 4AMECHMAX_ILR | 4A | People dissatisfied | MECH | MAX_ILR | Percentage (%) | 5 | 06:30,30/Nov | 73 | 15:30,01/Aug | 25
[13 empty] | 4AFLOOR 2MAX_ILR | 4A | People dissatisfied | FLOOR 2 | MAX_ILR | Percentage (%) | 5 | 07:30,07/Jan | 61 | 13:30,31/Jul | 20
[13 empty] | 4AAUDITORIUMMAX_ILR | 4A | People dissatisfied | AUDITORIUM | MAX_ILR | Percentage (%) | 5 | 02:30,06/Jan | 65 | 14:30,31/Jul | 19
[13 empty] | 4AGYMMAX_ILR | 4A | People dissatisfied | GYM | MAX_ILR | Percentage (%) | 5 | 11:30,27/Nov | 48 | 21:30,04/Jul | 13
[13 empty] | 4AKITCHEN CAFETERIAMAX_ILR | 4A | People dissatisfied | KITCHEN CAFETERIA | MAX_ILR | Percentage (%) | 5 | 17:30,16/Feb | 60 | 01:30,02/Aug | 19
[13 empty] | 4BLocationFilename | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 4BFLOOR 1TMY3_ILR | 4B | People dissatisfied | FLOOR 1 | TMY3_ILR | Percentage (%) | 5 | 07:30,10/May | 41 | 15:30,25/Jul | 14
[13 empty] | 4BMECHTMY3_ILR | 4B | People dissatisfied | MECH | TMY3_ILR | Percentage (%) | 5 | 01:30,10/May | 57 | 14:30,29/Jun | 19
[13 empty] | 4BFLOOR 2TMY3_ILR | 4B | People dissatisfied | FLOOR 2 | TMY3_ILR | Percentage (%) | 5 | 06:30,14/May | 50 | 16:30,21/Aug | 15
[13 empty] | 4BAUDITORIUMTMY3_ILR | 4B | People dissatisfied | AUDITORIUM | TMY3_ILR | Percentage (%) | 5 | 08:30,12/Oct | 52 | 15:30,08/Aug | 15
[13 empty] | 4BGYMTMY3_ILR | 4B | People dissatisfied | GYM | TMY3_ILR | Percentage (%) | 5 | 10:30,22/Feb | 59 | 18:30,20/May | 14
[13 empty] | 4BKITCHEN CAFETERIATMY3_ILR | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY3_ILR | Percentage (%) | 5 | 15:30,16/Dec | 39 | 18:30,25/Jul | 12
[13 empty] | 4BFLOOR 1TMY2_ILR | 4B | People dissatisfied | FLOOR 1 | TMY2_ILR | Percentage (%) | 5 | 06:30,11/May | 44 | 16:30,01/Aug | 14
[13 empty] | 4BMECHTMY2_ILR | 4B | People dissatisfied | MECH | TMY2_ILR | Percentage (%) | 5 | 23:30,07/Oct | 57 | 16:30,01/Aug | 19
[13 empty] | 4BFLOOR 2TMY2_ILR | 4B | People dissatisfied | FLOOR 2 | TMY2_ILR | Percentage (%) | 5 | 07:30,15/Oct | 52 | 15:30,01/Aug | 16
[13 empty] | 4BAUDITORIUMTMY2_ILR | 4B | People dissatisfied | AUDITORIUM | TMY2_ILR | Percentage (%) | 5 | 20:30,08/May | 53 | 15:30,01/Aug | 15
[13 empty] | 4BGYMTMY2_ILR | 4B | People dissatisfied | GYM | TMY2_ILR | Percentage (%) | 5 | 11:30,19/Jan | 59 | 18:30,21/May | 13
[13 empty] | 4BKITCHEN CAFETERIATMY2_ILR | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY2_ILR | Percentage (%) | 5 | 19:30,17/Mar | 48 | 19:30,01/Aug | 12
[13 empty] | 4BFLOOR 1TMY3WA_ILR | 4B | People dissatisfied | FLOOR 1 | TMY3WA_ILR | Percentage (%) | 5 | 06:30,07/May | 38 | 15:30,01/Aug | 13
[13 empty] | 4BMECHTMY3WA_ILR | 4B | People dissatisfied | MECH | TMY3WA_ILR | Percentage (%) | 5 | 11:30,02/Oct | 60 | 14:30,06/Jul | 19
[13 empty] | 4BFLOOR 2TMY3WA_ILR | 4B | People dissatisfied | FLOOR 2 | TMY3WA_ILR | Percentage (%) | 5 | 06:30,07/Jun | 54 | 12:30,11/Jul | 15
[13 empty] | 4BAUDITORIUMTMY3WA_ILR | 4B | People dissatisfied | AUDITORIUM | TMY3WA_ILR | Percentage (%) | 5 | 03:30,31/May | 54 | 11:30,11/Jul | 14
[13 empty] | 4BGYMTMY3WA_ILR | 4B | People dissatisfied | GYM | TMY3WA_ILR | Percentage (%) | 5 | 12:30,24/Nov | 56 | 18:30,19/May | 14
[13 empty] | 4BKITCHEN CAFETERIATMY3WA_ILR | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA_ILR | Percentage (%) | 5 | 16:30,03/Mar | 38 | 04:30,29/Nov | 12
[13 empty] | 4BFLOOR 1TMY7WA_ILR | 4B | People dissatisfied | FLOOR 1 | TMY7WA_ILR | Percentage (%) | 5 | 06:30,31/May | 38 | 14:30,18/Jul | 13
[13 empty] | 4BMECHTMY7WA_ILR | 4B | People dissatisfied | MECH | TMY7WA_ILR | Percentage (%) | 5 | 08:30,17/May | 64 | 14:30,20/Jul | 19
[13 empty] | 4BFLOOR 2TMY7WA_ILR | 4B | People dissatisfied | FLOOR 2 | TMY7WA_ILR | Percentage (%) | 5 | 06:30,26/May | 49 | 13:30,18/Jul | 15
[13 empty] | 4BAUDITORIUMTMY7WA_ILR | 4B | People dissatisfied | AUDITORIUM | TMY7WA_ILR | Percentage (%) | 5 | 00:30,03/Jun | 52 | 14:30,03/Jul | 14
[13 empty] | 4BGYMTMY7WA_ILR | 4B | People dissatisfied | GYM | TMY7WA_ILR | Percentage (%) | 5 | 13:30,07/Jan | 56 | 18:30,03/Sep | 13
[13 empty] | 4BKITCHEN CAFETERIATMY7WA_ILR | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA_ILR | Percentage (%) | 5 | 17:30,17/Feb | 39 | 19:30,18/Jul | 12
[13 empty] | 4BFLOOR 1TMY15WA_ILR | 4B | People dissatisfied | FLOOR 1 | TMY15WA_ILR | Percentage (%) | 5 | 06:30,07/May | 38 | 14:30,18/Jul | 13
[13 empty] | 4BMECHTMY15WA_ILR | 4B | People dissatisfied | MECH | TMY15WA_ILR | Percentage (%) | 5 | 23:30,26/Apr | 64 | 13:30,20/Jul | 19
[13 empty] | 4BFLOOR 2TMY15WA_ILR | 4B | People dissatisfied | FLOOR 2 | TMY15WA_ILR | Percentage (%) | 5 | 07:30,14/Sep | 49 | 13:30,18/Jul | 15
[13 empty] | 4BAUDITORIUMTMY15WA_ILR | 4B | People dissatisfied | AUDITORIUM | TMY15WA_ILR | Percentage (%) | 5 | 21:30,26/Apr | 50 | 13:30,27/Jun | 14
[13 empty] | 4BGYMTMY15WA_ILR | 4B | People dissatisfied | GYM | TMY15WA_ILR | Percentage (%) | 5 | 14:30,20/Dec | 56 | 18:30,19/May | 14
[13 empty] | 4BKITCHEN CAFETERIATMY15WA_ILR | 4B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA_ILR | Percentage (%) | 5 | 10:30,20/Dec | 39 | 19:30,18/Jul | 12
[13 empty] | 4BFLOOR 1MIN_ILR | 4B | People dissatisfied | FLOOR 1 | MIN_ILR | Percentage (%) | 5 | 06:30,17/Jun | 42 | 04:30,03/Feb | 15
[13 empty] | 4BMECHMIN_ILR | 4B | People dissatisfied | MECH | MIN_ILR | Percentage (%) | 5 | 23:30,16/Sep | 73 | 06:30,03/Feb | 20
[13 empty] | 4BFLOOR 2MIN_ILR | 4B | People dissatisfied | FLOOR 2 | MIN_ILR | Percentage (%) | 5 | 07:30,09/Jun | 45 | 04:30,03/Feb | 16
[13 empty] | 4BAUDITORIUMMIN_ILR | 4B | People dissatisfied | AUDITORIUM | MIN_ILR | Percentage (%) | 5 | 20:30,05/Nov | 45 | 06:30,04/Feb | 16
[13 empty] | 4BGYMMIN_ILR | 4B | People dissatisfied | GYM | MIN_ILR | Percentage (%) | 5 | 13:30,22/Mar | 51 | 19:30,31/May | 12
[13 empty] | 4BKITCHEN CAFETERIAMIN_ILR | 4B | People dissatisfied | KITCHEN CAFETERIA | MIN_ILR | Percentage (%) | 5 | 19:30,11/Oct | 40 | 05:30,03/Feb | 12
[13 empty] | 4BFLOOR 1MAX_ILR | 4B | People dissatisfied | FLOOR 1 | MAX_ILR | Percentage (%) | 5 | 07:30,22/Apr | 42 | 17:30,18/Jul | 13
[13 empty] | 4BMECHMAX_ILR | 4B | People dissatisfied | MECH | MAX_ILR | Percentage (%) | 5 | 23:30,28/Oct | 67 | 14:30,20/Jul | 21
[13 empty] | 4BFLOOR 2MAX_ILR | 4B | People dissatisfied | FLOOR 2 | MAX_ILR | Percentage (%) | 5 | 07:30,12/May | 51 | 14:30,18/Jul | 15
[13 empty] | 4BAUDITORIUMMAX_ILR | 4B | People dissatisfied | AUDITORIUM | MAX_ILR | Percentage (%) | 5 | 19:30,27/Dec | 52 | 14:30,18/Jul | 14
[13 empty] | 4BGYMMAX_ILR | 4B | People dissatisfied | GYM | MAX_ILR | Percentage (%) | 5 | 10:30,13/Dec | 65 | 19:30,31/May | 17
[13 empty] | 4BKITCHEN CAFETERIAMAX_ILR | 4B | People dissatisfied | KITCHEN CAFETERIA | MAX_ILR | Percentage (%) | 5 | 20:30,17/Feb | 44 | 18:30,18/Jul | 12
[13 empty] | 4CLocationFilename | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 4CFLOOR 1TMY3 ILR | 4C | People dissatisfied | FLOOR 1 | TMY3 ILR | Percentage (%) | 5 | 07:30,18/May | 30 | 19:30,10/Aug | 11
[13 empty] | 4CMECHTMY3 ILR | 4C | People dissatisfied | MECH | TMY3 ILR | Percentage (%) | 5 | 04:30,23/Sep | 34 | 18:30,21/Jul | 13
[13 empty] | 4CFLOOR 2TMY3 ILR | 4C | People dissatisfied | FLOOR 2 | TMY3 ILR | Percentage (%) | 5 | 07:30,07/Oct | 46 | 16:30,05/Jun | 12
[13 empty] | 4CAUDITORIUMTMY3 ILR | 4C | People dissatisfied | AUDITORIUM | TMY3 ILR | Percentage (%) | 5 | 14:30,26/Feb | 39 | 23:30,24/Jan | 12
[13 empty] | 4CGYMTMY3 ILR | 4C | People dissatisfied | GYM | TMY3 ILR | Percentage (%) | 5 | 11:30,16/May | 44 | 18:30,07/Oct | 9
[13 empty] | 4CKITCHEN CAFETERIATMY3 ILR | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY3 ILR | Percentage (%) | 5 | 20:30,16/Mar | 30 | 19:30,08/Aug | 10
[13 empty] | 4CFLOOR 1TMY3WA ILR | 4C | People dissatisfied | FLOOR 1 | TMY3WA ILR | Percentage (%) | 5 | 07:30,13/Oct | 30 | 04:30,31/Dec | 10
[13 empty] | 4CMECHTMY3WA ILR | 4C | People dissatisfied | MECH | TMY3WA ILR | Percentage (%) | 5 | 09:30,25/Aug | 35 | 05:30,31/Dec | 13
[13 empty] | 4CFLOOR 2TMY3WA ILR | 4C | People dissatisfied | FLOOR 2 | TMY3WA ILR | Percentage (%) | 5 | 06:30,14/Sep | 47 | 16:30,11/Jul | 12
[13 empty] | 4CAUDITORIUMTMY3WA ILR | 4C | People dissatisfied | AUDITORIUM | TMY3WA ILR | Percentage (%) | 5 | 13:30,14/Jan | 41 | 04:30,31/Dec | 11
[13 empty] | 4CGYMTMY3WA ILR | 4C | People dissatisfied | GYM | TMY3WA ILR | Percentage (%) | 5 | 09:30,13/Nov | 49 | 17:30,06/Sep | 9
[13 empty] | 4CKITCHEN CAFETERIATMY3WA ILR | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA ILR | Percentage (%) | 5 | 13:30,27/Mar | 26 | 10:30,17/May | 9
[13 empty] | 4CFLOOR 1TMY7WA ILR | 4C | People dissatisfied | FLOOR 1 | TMY7WA ILR | Percentage (%) | 5 | 06:30,01/Sep | 37 | 15:30,01/Aug | 11
[13 empty] | 4CMECHTMY7WA ILR | 4C | People dissatisfied | MECH | TMY7WA ILR | Percentage (%) | 5 | 23:30,29/Sep | 48 | 14:30,29/Jul | 15
[13 empty] | 4CFLOOR 2TMY7WA ILR | 4C | People dissatisfied | FLOOR 2 | TMY7WA ILR | Percentage (%) | 5 | 15:30,06/Jan | 52 | 15:30,01/Aug | 13
[13 empty] | 4CAUDITORIUMTMY7WA ILR | 4C | People dissatisfied | AUDITORIUM | TMY7WA ILR | Percentage (%) | 5 | 10:30,27/Apr | 55 | 16:30,31/Jul | 12
[13 empty] | 4CGYMTMY7WA ILR | 4C | People dissatisfied | GYM | TMY7WA ILR | Percentage (%) | 5 | 08:30,07/Apr | 41 | 17:30,05/May | 10
[13 empty] | 4CKITCHEN CAFETERIATMY7WA ILR | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA ILR | Percentage (%) | 5 | 17:30,17/Nov | 34 | 19:30,01/Aug | 9
[13 empty] | 4CFLOOR 1TMY2 ILR | 4C | People dissatisfied | FLOOR 1 | TMY2 ILR | Percentage (%) | 5 | 06:30,25/May | 33 | 05:30,31/Jan | 11
[13 empty] | 4CMECHTMY2 ILR | 4C | People dissatisfied | MECH | TMY2 ILR | Percentage (%) | 5 | 04:30,23/Sep | 38 | 02:30,31/Jan | 13
[13 empty] | 4CFLOOR 2TMY2 ILR | 4C | People dissatisfied | FLOOR 2 | TMY2 ILR | Percentage (%) | 5 | 07:30,09/Apr | 42 | 15:30,24/Jul | 12
[13 empty] | 4CAUDITORIUMTMY2 ILR | 4C | People dissatisfied | AUDITORIUM | TMY2 ILR | Percentage (%) | 5 | 15:30,11/Jan | 42 | 05:30,27/Dec | 12
[13 empty] | 4CGYMTMY2 ILR | 4C | People dissatisfied | GYM | TMY2 ILR | Percentage (%) | 5 | 10:30,30/Oct | 51 | 18:30,17/May | 9
[13 empty] | 4CKITCHEN CAFETERIATMY2 ILR | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY2 ILR | Percentage (%) | 5 | 20:30,12/Feb | 30 | 19:30,15/Aug | 9
[13 empty] | 4CFLOOR 1MIN ILR | 4C | People dissatisfied | FLOOR 1 | MIN ILR | Percentage (%) | 5 | 07:30,18/Aug | 36 | 06:30,07/Feb | 15
[13 empty] | 4CMECHMIN ILR | 4C | People dissatisfied | MECH | MIN ILR | Percentage (%) | 5 | 13:30,28/Jul | 50 | 07:30,07/Feb | 21
[13 empty] | 4CFLOOR 2MIN ILR | 4C | People dissatisfied | FLOOR 2 | MIN ILR | Percentage (%) | 5 | 11:30,10/Jun | 36 | 04:30,08/Dec | 15
[13 empty] | 4CAUDITORIUMMIN ILR | 4C | People dissatisfied | AUDITORIUM | MIN ILR | Percentage (%) | 5 | 12:30,20/May | 43 | 06:30,31/Oct | 16
[13 empty] | 4CGYMMIN ILR | 4C | People dissatisfied | GYM | MIN ILR | Percentage (%) | 5 | 09:30,05/Apr | 40 | 07:30,07/Feb | 11
[13 empty] | 4CKITCHEN CAFETERIAMIN ILR | 4C | People dissatisfied | KITCHEN CAFETERIA | MIN ILR | Percentage (%) | 5 | 13:30,25/Feb | 38 | 05:30,07/Feb | 10
[13 empty] | 4CFLOOR 1TMY15WA ILR | 4C | People dissatisfied | FLOOR 1 | TMY15WA ILR | Percentage (%) | 5 | 06:30,01/Sep | 37 | 15:30,01/Aug | 11
[13 empty] | 4CMECHTMY15WA ILR | 4C | People dissatisfied | MECH | TMY15WA ILR | Percentage (%) | 5 | 23:30,29/Sep | 48 | 14:30,29/Jul | 14
[13 empty] | 4CFLOOR 2TMY15WA ILR | 4C | People dissatisfied | FLOOR 2 | TMY15WA ILR | Percentage (%) | 5 | 07:30,29/Sep | 52 | 15:30,01/Aug | 13
[13 empty] | 4CAUDITORIUMTMY15WA ILR | 4C | People dissatisfied | AUDITORIUM | TMY15WA ILR | Percentage (%) | 5 | 13:30,14/Jan | 54 | 16:30,31/Jul | 12
[13 empty] | 4CGYMTMY15WA ILR | 4C | People dissatisfied | GYM | TMY15WA ILR | Percentage (%) | 5 | 17:30,20/Mar | 41 | 17:30,03/Sep | 9
[13 empty] | 4CKITCHEN CAFETERIATMY15WA ILR | 4C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA ILR | Percentage (%) | 5 | 19:30,04/Jan | 34 | 19:30,01/Aug | 9
[13 empty] | 4CFLOOR 1MAX ILR | 4C | People dissatisfied | FLOOR 1 | MAX ILR | Percentage (%) | 5 | 07:30,09/Apr | 40 | 18:30,15/Aug | 12
[13 empty] | 4CMECHMAX ILR | 4C | People dissatisfied | MECH | MAX ILR | Percentage (%) | 5 | 09:30,28/Oct | 51 | 15:30,29/Jul | 14
[13 empty] | 4CFLOOR 2MAX ILR | 4C | People dissatisfied | FLOOR 2 | MAX ILR | Percentage (%) | 5 | 07:30,07/Apr | 54 | 16:30,15/Aug | 14
[13 empty] | 4CAUDITORIUMMAX ILR | 4C | People dissatisfied | AUDITORIUM | MAX ILR | Percentage (%) | 5 | 10:30,25/Feb | 54 | 14:30,25/Jul | 12
[13 empty] | 4CGYMMAX ILR | 4C | People dissatisfied | GYM | MAX ILR | Percentage (%) | 5 | 12:30,03/Jan | 56 | 17:30,06/Sep | 11
[13 empty] | 4CKITCHEN CAFETERIAMAX ILR | 4C | People dissatisfied | KITCHEN CAFETERIA | MAX ILR | Percentage (%) | 5 | 14:30,03/Jan | 44 | 19:30,15/Aug | 11
[13 empty] | 5ALocationFilename | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 5AFLOOR 1MAX_ILR | 5A | People dissatisfied | FLOOR 1 | MAX_ILR | Percentage (%) | 5 | 07:30,08/Apr | 53 | 02:30,19/Jul | 16
[13 empty] | 5AMECHMAX_ILR | 5A | People dissatisfied | MECH | MAX_ILR | Percentage (%) | 5 | 01:30,27/Apr | 66 | 14:30,06/Jul | 20
[13 empty] | 5AFLOOR 2MAX_ILR | 5A | People dissatisfied | FLOOR 2 | MAX_ILR | Percentage (%) | 5 | 07:30,01/Nov | 57 | 15:30,07/Aug | 18
[13 empty] | 5AAUDITORIUMMAX_ILR | 5A | People dissatisfied | AUDITORIUM | MAX_ILR | Percentage (%) | 5 | 15:30,07/Dec | 63 | 16:30,22/Aug | 16
[13 empty] | 5AGYMMAX_ILR | 5A | People dissatisfied | GYM | MAX_ILR | Percentage (%) | 5 | 11:30,18/Jan | 43 | 01:30,26/Jul | 11
[13 empty] | 5AKITCHEN CAFETERIAMAX_ILR | 5A | People dissatisfied | KITCHEN CAFETERIA | MAX_ILR | Percentage (%) | 5 | 16:30,22/Jan | 59 | 19:30,01/Aug | 16
[13 empty] | 5AFLOOR 1MIN_ILR | 5A | People dissatisfied | FLOOR 1 | MIN_ILR | Percentage (%) | 5 | 02:30,06/Jul | 43 | 07:30,31/Jan | 16
[13 empty] | 5AMECHMIN_ILR | 5A | People dissatisfied | MECH | MIN_ILR | Percentage (%) | 5 | 00:30,07/Sep | 45 | 06:30,31/Jan | 22
[13 empty] | 5AFLOOR 2MIN_ILR | 5A | People dissatisfied | FLOOR 2 | MIN_ILR | Percentage (%) | 5 | 07:30,24/Sep | 42 | 07:30,16/Jan | 17
[13 empty] | 5AAUDITORIUMMIN_ILR | 5A | People dissatisfied | AUDITORIUM | MIN_ILR | Percentage (%) | 5 | 20:30,17/Mar | 46 | 03:30,08/Feb | 16
[13 empty] | 5AGYMMIN_ILR | 5A | People dissatisfied | GYM | MIN_ILR | Percentage (%) | 5 | 16:30,09/May | 47 | 04:30,31/Jan | 12
[13 empty] | 5AKITCHEN CAFETERIAMIN_ILR | 5A | People dissatisfied | KITCHEN CAFETERIA | MIN_ILR | Percentage (%) | 5 | 10:30,18/Sep | 39 | 03:30,22/Nov | 13
[13 empty] | 5AFLOOR 1TMY15WA_ILR | 5A | People dissatisfied | FLOOR 1 | TMY15WA_ILR | Percentage (%) | 5 | 07:30,30/Sep | 45 | 12:30,24/Jul | 15
[13 empty] | 5AMECHTMY15WA_ILR | 5A | People dissatisfied | MECH | TMY15WA_ILR | Percentage (%) | 5 | 20:30,16/Oct | 54 | 16:30,21/Jul | 19
[13 empty] | 5AFLOOR 2TMY15WA_ILR | 5A | People dissatisfied | FLOOR 2 | TMY15WA_ILR | Percentage (%) | 5 | 07:30,29/Sep | 56 | 13:30,01/Aug | 16
[13 empty] | 5AAUDITORIUMTMY15WA_ILR | 5A | People dissatisfied | AUDITORIUM | TMY15WA_ILR | Percentage (%) | 5 | 14:30,12/Nov | 66 | 14:30,18/Jul | 16
[13 empty] | 5AGYMTMY15WA_ILR | 5A | People dissatisfied | GYM | TMY15WA_ILR | Percentage (%) | 5 | 14:30,06/Dec | 39 | 07:30,05/Dec | 11
[13 empty] | 5AKITCHEN CAFETERIATMY15WA_ILR | 5A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA_ILR | Percentage (%) | 5 | 12:30,03/Feb | 49 | 01:30,19/Jul | 14
[13 empty] | 5AFLOOR 1TMY7WA_ILR | 5A | People dissatisfied | FLOOR 1 | TMY7WA_ILR | Percentage (%) | 5 | 07:30,27/Oct | 45 | 12:30,24/Jul | 15
[13 empty] | 5AMECHTMY7WA_ILR | 5A | People dissatisfied | MECH | TMY7WA_ILR | Percentage (%) | 5 | 00:30,16/May | 54 | 16:30,21/Jul | 19
[13 empty] | 5AFLOOR 2TMY7WA_ILR | 5A | People dissatisfied | FLOOR 2 | TMY7WA_ILR | Percentage (%) | 5 | 07:30,14/Oct | 56 | 13:30,01/Aug | 16
[13 empty] | 5AAUDITORIUMTMY7WA_ILR | 5A | People dissatisfied | AUDITORIUM | TMY7WA_ILR | Percentage (%) | 5 | 19:30,06/Jan | 66 | 14:30,18/Jul | 16
[13 empty] | 5AGYMTMY7WA_ILR | 5A | People dissatisfied | GYM | TMY7WA_ILR | Percentage (%) | 5 | 11:30,18/Jan | 43 | 07:30,24/Jan | 11
[13 empty] | 5AKITCHEN CAFETERIATMY7WA_ILR | 5A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA_ILR | Percentage (%) | 5 | 13:30,01/Mar | 49 | 01:30,19/Jul | 13
[13 empty] | 5AFLOOR 1TMY3WA_ILR | 5A | People dissatisfied | FLOOR 1 | TMY3WA_ILR | Percentage (%) | 5 | 07:30,30/Sep | 48 | 14:30,18/Jul | 14
[13 empty] | 5AMECHTMY3WA_ILR | 5A | People dissatisfied | MECH | TMY3WA_ILR | Percentage (%) | 5 | 20:30,16/Oct | 53 | 14:30,16/Aug | 18
[13 empty] | 5AFLOOR 2TMY3WA_ILR | 5A | People dissatisfied | FLOOR 2 | TMY3WA_ILR | Percentage (%) | 5 | 07:30,29/Sep | 55 | 15:30,14/Aug | 16
[13 empty] | 5AAUDITORIUMTMY3WA_ILR | 5A | People dissatisfied | AUDITORIUM | TMY3WA_ILR | Percentage (%) | 5 | 14:30,12/Nov | 62 | 15:30,18/Jul | 15
[13 empty] | 5AGYMTMY3WA_ILR | 5A | People dissatisfied | GYM | TMY3WA_ILR | Percentage (%) | 5 | 14:30,06/Dec | 39 | 07:30,05/Dec | 10
[13 empty] | 5AKITCHEN CAFETERIATMY3WA_ILR | 5A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA_ILR | Percentage (%) | 5 | 13:30,24/Oct | 49 | 05:30,16/Aug | 13
[13 empty] | 5AFLOOR 1TMY3_ILR | 5A | People dissatisfied | FLOOR 1 | TMY3_ILR | Percentage (%) | 5 | 07:30,07/May | 49 | 22:30,18/Jul | 15
[13 empty] | 5AMECHTMY3_ILR | 5A | People dissatisfied | MECH | TMY3_ILR | Percentage (%) | 5 | 00:30,22/May | 54 | 18:30,18/Jul | 19
[13 empty] | 5AFLOOR 2TMY3_ILR | 5A | People dissatisfied | FLOOR 2 | TMY3_ILR | Percentage (%) | 5 | 07:30,20/Apr | 56 | 13:30,18/Jul | 16
[13 empty] | 5AAUDITORIUMTMY3_ILR | 5A | People dissatisfied | AUDITORIUM | TMY3_ILR | Percentage (%) | 5 | 16:30,20/Jan | 64 | 13:30,17/Jul | 16
[13 empty] | 5AGYMTMY3_ILR | 5A | People dissatisfied | GYM | TMY3_ILR | Percentage (%) | 5 | 12:30,17/Feb | 47 | 02:30,07/Feb | 11
[13 empty] | 5AKITCHEN CAFETERIATMY3_ILR | 5A | People dissatisfied | KITCHEN CAFETERIA | TMY3_ILR | Percentage (%) | 5 | 18:30,17/Nov | 56 | 21:30,18/Jul | 14
[13 empty] | 5AFLOOR 1TMY2_ILR | 5A | People dissatisfied | FLOOR 1 | TMY2_ILR | Percentage (%) | 5 | 07:30,07/May | 41 | 15:30,04/Jul | 15
[13 empty] | 5AMECHTMY2_ILR | 5A | People dissatisfied | MECH | TMY2_ILR | Percentage (%) | 5 | 00:30,22/May | 45 | 14:30,19/Jul | 19
[13 empty] | 5AFLOOR 2TMY2_ILR | 5A | People dissatisfied | FLOOR 2 | TMY2_ILR | Percentage (%) | 5 | 07:30,01/Apr | 52 | 13:30,03/Jul | 16
[13 empty] | 5AAUDITORIUMTMY2_ILR | 5A | People dissatisfied | AUDITORIUM | TMY2_ILR | Percentage (%) | 5 | 22:30,04/Oct | 59 | 16:30,03/Jul | 16
[13 empty] | 5AGYMTMY2_ILR | 5A | People dissatisfied | GYM | TMY2_ILR | Percentage (%) | 5 | 14:30,25/Feb | 41 | 05:30,08/Feb | 11
[13 empty] | 5AKITCHEN CAFETERIATMY2_ILR | 5A | People dissatisfied | KITCHEN CAFETERIA | TMY2_ILR | Percentage (%) | 5 | 19:30,13/Apr | 45 | 20:30,18/Jul | 13
[13 empty] | 5BLocationFilename | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 5BFLOOR 1TMY2_ILR | 5B | People dissatisfied | FLOOR 1 | TMY2_ILR | Percentage (%) | 5 | 06:30,04/Jun | 42 | 04:30,13/Dec | 13
[13 empty] | 5BMECHTMY2_ILR | 5B | People dissatisfied | MECH | TMY2_ILR | Percentage (%) | 5 | 09:30,05/Oct | 48 | 15:30,18/Jul | 18
[13 empty] | 5BFLOOR 2TMY2_ILR | 5B | People dissatisfied | FLOOR 2 | TMY2_ILR | Percentage (%) | 5 | 07:30,14/Sep | 48 | 15:30,18/Jul | 15
[13 empty] | 5BAUDITORIUMTMY2_ILR | 5B | People dissatisfied | AUDITORIUM | TMY2_ILR | Percentage (%) | 5 | 16:30,22/Feb | 50 | 14:30,04/Jul | 15
[13 empty] | 5BGYMTMY2_ILR | 5B | People dissatisfied | GYM | TMY2_ILR | Percentage (%) | 5 | 13:30,15/Jan | 62 | 18:30,02/Sep | 13
[13 empty] | 5BKITCHEN CAFETERIATMY2_ILR | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY2_ILR | Percentage (%) | 5 | 19:30,05/Apr | 39 | 03:30,14/Dec | 11
[13 empty] | 5BFLOOR 1TMY3_ILR | 5B | People dissatisfied | FLOOR 1 | TMY3_ILR | Percentage (%) | 5 | 11:30,09/Jun | 42 | 04:30,13/Dec | 13
[13 empty] | 5BMECHTMY3_ILR | 5B | People dissatisfied | MECH | TMY3_ILR | Percentage (%) | 5 | 00:30,01/May | 46 | 15:30,14/Jul | 18
[13 empty] | 5BFLOOR 2TMY3_ILR | 5B | People dissatisfied | FLOOR 2 | TMY3_ILR | Percentage (%) | 5 | 06:30,06/Sep | 46 | 13:30,01/Aug | 15
[13 empty] | 5BAUDITORIUMTMY3_ILR | 5B | People dissatisfied | AUDITORIUM | TMY3_ILR | Percentage (%) | 5 | 11:30,25/Apr | 46 | 05:30,17/Jan | 14
[13 empty] | 5BGYMTMY3_ILR | 5B | People dissatisfied | GYM | TMY3_ILR | Percentage (%) | 5 | 11:30,14/Jan | 59 | 19:30,28/May | 13
[13 empty] | 5BKITCHEN CAFETERIATMY3_ILR | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY3_ILR | Percentage (%) | 5 | 16:30,14/Apr | 39 | 02:30,18/Jan | 11
[13 empty] | 5BFLOOR 1TMY3WA_ILR | 5B | People dissatisfied | FLOOR 1 | TMY3WA_ILR | Percentage (%) | 5 | 06:30,10/Sep | 38 | 04:30,24/Dec | 14
[13 empty] | 5BMECHTMY3WA_ILR | 5B | People dissatisfied | MECH | TMY3WA_ILR | Percentage (%) | 5 | 08:30,12/Jun | 41 | 04:30,24/Dec | 18
[13 empty] | 5BFLOOR 2TMY3WA_ILR | 5B | People dissatisfied | FLOOR 2 | TMY3WA_ILR | Percentage (%) | 5 | 07:30,10/Sep | 50 | 15:30,18/Jul | 15
[13 empty] | 5BAUDITORIUMTMY3WA_ILR | 5B | People dissatisfied | AUDITORIUM | TMY3WA_ILR | Percentage (%) | 5 | 16:30,29/May | 52 | 13:30,01/Aug | 15
[13 empty] | 5BGYMTMY3WA_ILR | 5B | People dissatisfied | GYM | TMY3WA_ILR | Percentage (%) | 5 | 15:30,11/Sep | 48 | 17:30,03/Sep | 12
[13 empty] | 5BKITCHEN CAFETERIATMY3WA_ILR | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA_ILR | Percentage (%) | 5 | 17:30,25/Oct | 38 | 03:30,18/Jan | 11
[13 empty] | 5BFLOOR 1TMY7WA_ILR | 5B | People dissatisfied | FLOOR 1 | TMY7WA_ILR | Percentage (%) | 5 | 06:30,10/Jun | 40 | 00:30,07/Feb | 14
[13 empty] | 5BMECHTMY7WA_ILR | 5B | People dissatisfied | MECH | TMY7WA_ILR | Percentage (%) | 5 | 22:30,21/Jun | 45 | 06:30,06/Feb | 18
[13 empty] | 5BFLOOR 2TMY7WA_ILR | 5B | People dissatisfied | FLOOR 2 | TMY7WA_ILR | Percentage (%) | 5 | 07:30,10/Sep | 50 | 15:30,18/Jul | 15
[13 empty] | 5BAUDITORIUMTMY7WA_ILR | 5B | People dissatisfied | AUDITORIUM | TMY7WA_ILR | Percentage (%) | 5 | 17:30,18/Jan | 52 | 13:30,01/Aug | 15
[13 empty] | 5BGYMTMY7WA_ILR | 5B | People dissatisfied | GYM | TMY7WA_ILR | Percentage (%) | 5 | 15:30,11/Sep | 48 | 17:30,03/Sep | 12
[13 empty] | 5BKITCHEN CAFETERIATMY7WA_ILR | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA_ILR | Percentage (%) | 5 | 17:30,25/Oct | 39 | 05:30,05/Jan | 11
[13 empty] | 5BFLOOR 1TMY15WA_ILR | 5B | People dissatisfied | FLOOR 1 | TMY15WA_ILR | Percentage (%) | 5 | 07:30,09/Sep | 38 | 04:30,24/Dec | 14
[13 empty] | 5BMECHTMY15WA_ILR | 5B | People dissatisfied | MECH | TMY15WA_ILR | Percentage (%) | 5 | 08:30,07/May | 41 | 04:30,24/Dec | 18
[13 empty] | 5BFLOOR 2TMY15WA_ILR | 5B | People dissatisfied | FLOOR 2 | TMY15WA_ILR | Percentage (%) | 5 | 07:30,24/Sep | 45 | 14:30,25/Jul | 15
[13 empty] | 5BAUDITORIUMTMY15WA_ILR | 5B | People dissatisfied | AUDITORIUM | TMY15WA_ILR | Percentage (%) | 5 | 17:30,03/Feb | 46 | 15:30,25/Jul | 15
[13 empty] | 5BGYMTMY15WA_ILR | 5B | People dissatisfied | GYM | TMY15WA_ILR | Percentage (%) | 5 | 09:30,12/Mar | 50 | 18:30,28/May | 12
[13 empty] | 5BKITCHEN CAFETERIATMY15WA_ILR | 5B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA_ILR | Percentage (%) | 5 | 17:30,25/Oct | 39 | 04:30,29/Nov | 11
[13 empty] | 5BFLOOR 1MIN_ILR | 5B | People dissatisfied | FLOOR 1 | MIN_ILR | Percentage (%) | 5 | 07:30,20/Jul | 44 | 03:30,06/Dec | 19
[13 empty] | 5BMECHMIN_ILR | 5B | People dissatisfied | MECH | MIN_ILR | Percentage (%) | 5 | 08:30,19/Jul | 58 | 05:30,02/Feb | 25
[13 empty] | 5BFLOOR 2MIN_ILR | 5B | People dissatisfied | FLOOR 2 | MIN_ILR | Percentage (%) | 5 | 07:30,26/Aug | 45 | 03:30,02/Feb | 19
[13 empty] | 5BAUDITORIUMMIN_ILR | 5B | People dissatisfied | AUDITORIUM | MIN_ILR | Percentage (%) | 5 | 16:30,29/Aug | 50 | 05:30,06/Dec | 19
[13 empty] | 5BGYMMIN_ILR | 5B | People dissatisfied | GYM | MIN_ILR | Percentage (%) | 5 | 14:30,06/Apr | 48 | 04:30,05/Dec | 13
[13 empty] | 5BKITCHEN CAFETERIAMIN_ILR | 5B | People dissatisfied | KITCHEN CAFETERIA | MIN_ILR | Percentage (%) | 5 | 19:30,08/Sep | 42 | 03:30,06/Dec | 14
[13 empty] | 5BFLOOR 1MAX_ILR | 5B | People dissatisfied | FLOOR 1 | MAX_ILR | Percentage (%) | 5 | 07:30,18/May | 31 | 14:30,25/Jul | 12
[13 empty] | 5BMECHMAX_ILR | 5B | People dissatisfied | MECH | MAX_ILR | Percentage (%) | 5 | 21:30,22/Oct | 44 | 15:30,15/Jul | 17
[13 empty] | 5BFLOOR 2MAX_ILR | 5B | People dissatisfied | FLOOR 2 | MAX_ILR | Percentage (%) | 5 | 06:30,08/Jun | 46 | 14:30,01/Aug | 14
[13 empty] | 5BAUDITORIUMMAX_ILR | 5B | People dissatisfied | AUDITORIUM | MAX_ILR | Percentage (%) | 5 | 16:30,25/Jan | 49 | 15:30,25/Jul | 14
[13 empty] | 5BGYMMAX_ILR | 5B | People dissatisfied | GYM | MAX_ILR | Percentage (%) | 5 | 10:30,03/Feb | 60 | 18:30,31/May | 13
[13 empty] | 5BKITCHEN CAFETERIAMAX_ILR | 5B | People dissatisfied | KITCHEN CAFETERIA | MAX_ILR | Percentage (%) | 5 | 17:30,02/Mar | 32 | 19:30,27/Jun | 11
[13 empty] | 5CLocationFilename | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 5CFLOOR 1doeCWEC_ILR | 5C | People dissatisfied | FLOOR 1 | doeCWEC_ILR | Percentage (%) | 5 | 07:30,13/May | 33 | 03:30,22/Nov | 11
[13 empty] | 5CMECHdoeCWEC_ILR | 5C | People dissatisfied | MECH | doeCWEC_ILR | Percentage (%) | 5 | 01:30,11/Jun | 35 | 04:30,22/Nov | 14
[13 empty] | 5CFLOOR 2doeCWEC_ILR | 5C | People dissatisfied | FLOOR 2 | doeCWEC_ILR | Percentage (%) | 5 | 07:30,13/May | 39 | 15:30,11/Jul | 12
[13 empty] | 5CAUDITORIUMdoeCWEC_ILR | 5C | People dissatisfied | AUDITORIUM | doeCWEC_ILR | Percentage (%) | 5 | 14:30,01/Apr | 42 | 17:30,21/Nov | 12
[13 empty] | 5CGYMdoeCWEC_ILR | 5C | People dissatisfied | GYM | doeCWEC_ILR | Percentage (%) | 5 | 13:30,17/Oct | 34 | 01:30,22/Nov | 9
[13 empty] | 5CKITCHEN CAFETERIAdoeCWEC_ILR | 5C | People dissatisfied | KITCHEN CAFETERIA | doeCWEC_ILR | Percentage (%) | 5 | 12:30,13/Dec | 26 | 03:30,22/Nov | 9
[13 empty] | 5CFLOOR 1TMY3WA_ILR | 5C | People dissatisfied | FLOOR 1 | TMY3WA_ILR | Percentage (%) | 5 | 23:30,08/Jun | 28 | 03:30,27/Dec | 10
[13 empty] | 5CMECHTMY3WA_ILR | 5C | People dissatisfied | MECH | TMY3WA_ILR | Percentage (%) | 5 | 09:30,05/Jul | 30 | 23:30,28/Dec | 12
[13 empty] | 5CFLOOR 2TMY3WA_ILR | 5C | People dissatisfied | FLOOR 2 | TMY3WA_ILR | Percentage (%) | 5 | 15:30,18/Feb | 43 | 15:30,25/Jul | 12
[13 empty] | 5CAUDITORIUMTMY3WA_ILR | 5C | People dissatisfied | AUDITORIUM | TMY3WA_ILR | Percentage (%) | 5 | 11:30,26/Jan | 35 | 05:30,27/Dec | 11
[13 empty] | 5CGYMTMY3WA_ILR | 5C | People dissatisfied | GYM | TMY3WA_ILR | Percentage (%) | 5 | 07:30,14/Jun | 48 | 17:30,28/May | 9
[13 empty] | 5CKITCHEN CAFETERIATMY3WA_ILR | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY3WA_ILR | Percentage (%) | 5 | 19:30,02/Dec | 26 | 10:30,10/Sep | 8
[13 empty] | 5CFLOOR 1TMY7WA_ILR | 5C | People dissatisfied | FLOOR 1 | TMY7WA_ILR | Percentage (%) | 5 | 19:30,26/Jun | 30 | 23:30,31/Jan | 11
[13 empty] | 5CMECHTMY7WA_ILR | 5C | People dissatisfied | MECH | TMY7WA_ILR | Percentage (%) | 5 | 08:30,23/Jul | 33 | 06:30,31/Dec | 14
[13 empty] | 5CFLOOR 2TMY7WA_ILR | 5C | People dissatisfied | FLOOR 2 | TMY7WA_ILR | Percentage (%) | 5 | 15:30,21/Jan | 32 | 14:30,03/Jul | 12
[13 empty] | 5CAUDITORIUMTMY7WA_ILR | 5C | People dissatisfied | AUDITORIUM | TMY7WA_ILR | Percentage (%) | 5 | 12:30,26/Feb | 41 | 20:30,31/Jan | 12
[13 empty] | 5CGYMTMY7WA_ILR | 5C | People dissatisfied | GYM | TMY7WA_ILR | Percentage (%) | 5 | 09:30,15/Nov | 30 | 02:30,01/Feb | 9
[13 empty] | 5CKITCHEN CAFETERIATMY7WA_ILR | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY7WA_ILR | Percentage (%) | 5 | 20:30,08/Mar | 25 | 10:30,06/Sep | 8
[13 empty] | 5CFLOOR 1TMY15WA_ILR | 5C | People dissatisfied | FLOOR 1 | TMY15WA_ILR | Percentage (%) | 5 | 07:30,04/Jul | 29 | 00:30,01/Nov | 11
[13 empty] | 5CMECHTMY15WA_ILR | 5C | People dissatisfied | MECH | TMY15WA_ILR | Percentage (%) | 5 | 14:30,28/Jun | 32 | 17:30,31/Oct | 13
[13 empty] | 5CFLOOR 2TMY15WA_ILR | 5C | People dissatisfied | FLOOR 2 | TMY15WA_ILR | Percentage (%) | 5 | 15:30,17/Dec | 51 | 15:30,11/Jul | 12
[13 empty] | 5CAUDITORIUMTMY15WA_ILR | 5C | People dissatisfied | AUDITORIUM | TMY15WA_ILR | Percentage (%) | 5 | 23:30,11/May | 42 | 15:30,11/Jul | 11
[13 empty] | 5CGYMTMY15WA_ILR | 5C | People dissatisfied | GYM | TMY15WA_ILR | Percentage (%) | 5 | 13:30,26/Sep | 31 | 03:30,01/Nov | 9
[13 empty] | 5CKITCHEN CAFETERIATMY15WA_ILR | 5C | People dissatisfied | KITCHEN CAFETERIA | TMY15WA_ILR | Percentage (%) | 5 | 19:30,23/Feb | 27 | 19:30,11/Jul | 8
[13 empty] | 5CFLOOR 1MAX_ILR | 5C | People dissatisfied | FLOOR 1 | MAX_ILR | Percentage (%) | 5 | 07:30,29/Apr | 27 | 15:30,11/Jul | 10
[13 empty] | 5CMECHMAX_ILR | 5C | People dissatisfied | MECH | MAX_ILR | Percentage (%) | 5 | 00:30,01/May | 33 | 15:30,11/Jul | 12
[13 empty] | 5CFLOOR 2MAX_ILR | 5C | People dissatisfied | FLOOR 2 | MAX_ILR | Percentage (%) | 5 | 07:30,28/Apr | 51 | 13:30,11/Jul | 12
[13 empty] | 5CAUDITORIUMMAX_ILR | 5C | People dissatisfied | AUDITORIUM | MAX_ILR | Percentage (%) | 5 | 13:30,04/Feb | 50 | 15:30,11/Jul | 11
[13 empty] | 5CGYMMAX_ILR | 5C | People dissatisfied | GYM | MAX_ILR | Percentage (%) | 5 | 15:30,10/Oct | 34 | 17:30,31/May | 9
[13 empty] | 5CKITCHEN CAFETERIAMAX_ILR | 5C | People dissatisfied | KITCHEN CAFETERIA | MAX_ILR | Percentage (%) | 5 | 17:30,22/Feb | 33 | 19:30,11/Jul | 9
[13 empty] | 5CFLOOR 1MIN_ILR | 5C | People dissatisfied | FLOOR 1 | MIN_ILR | Percentage (%) | 5 | 17:30,15/Jul | 38 | 03:30,20/Dec | 15
[13 empty] | 5CMECHMIN_ILR | 5C | People dissatisfied | MECH | MIN_ILR | Percentage (%) | 5 | 20:30,09/Sep | 52 | 04:30,20/Dec | 20
[13 empty] | 5CFLOOR 2MIN_ILR | 5C | People dissatisfied | FLOOR 2 | MIN_ILR | Percentage (%) | 5 | 16:30,09/Jun | 39 | 03:30,04/Jan | 15
[13 empty] | 5CAUDITORIUMMIN_ILR | 5C | People dissatisfied | AUDITORIUM | MIN_ILR | Percentage (%) | 5 | 14:30,26/Mar | 43 | 05:30,20/Dec | 15
[13 empty] | 5CGYMMIN_ILR | 5C | People dissatisfied | GYM | MIN_ILR | Percentage (%) | 5 | 14:30,08/Feb | 44 | 04:30,29/Nov | 11
[13 empty] | 5CKITCHEN CAFETERIAMIN_ILR | 5C | People dissatisfied | KITCHEN CAFETERIA | MIN_ILR | Percentage (%) | 5 | 12:30,10/Feb | 38 | 03:30,19/Dec | 10
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 5C | 5C
[13 empty] | 6ALocationFilename | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 6AFLOOR 1TMY2 | 6A | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,21/May | 45 | 15:30,18/Jul | 15
[13 empty] | 6AMECHTMY2 | 6A | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 10:30,09/Oct | 45 | 00:30,10/Jan | 20
[13 empty] | 6AFLOOR 2TMY2 | 6A | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,21/May | 54 | 17:30,11/Jul | 17
[13 empty] | 6AAUDITORIUMTMY2 | 6A | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 07:30,13/Sep | 59 | 16:30,18/Jul | 16
[13 empty] | 6AGYMTMY2 | 6A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 16:30,29/Jan | 49 | 04:30,10/Jan | 11
[13 empty] | 6AKITCHEN CAFETERIATMY2 | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 16:30,24/Mar | 45 | 07:30,18/Jul | 14
[13 empty] | 6AFLOOR 1TMY3 | 6A | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,14/May | 49 | 13:30,04/Jul | 16
[13 empty] | 6AMECHTMY3 | 6A | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 09:30,16/May | 51 | 19:30,18/Jul | 21
[13 empty] | 6AFLOOR 2TMY3 | 6A | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,13/May | 57 | 11:30,04/Jul | 17
[13 empty] | 6AAUDITORIUMTMY3 | 6A | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 18:30,12/Jan | 66 | 13:30,04/Jul | 17
[13 empty] | 6AGYMTMY3 | 6A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 10:30,26/Mar | 49 | 07:30,12/Dec | 12
[13 empty] | 6AKITCHEN CAFETERIATMY3 | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 08:30,07/May | 54 | 21:30,18/Jul | 14
[13 empty] | 6AFLOOR 1TMY3WA | 6A | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,30/Sep | 52 | 11:30,18/Jul | 14
[13 empty] | 6AMECHTMY3WA | 6A | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 19:30,08/May | 59 | 18:30,18/Jul | 19
[13 empty] | 6AFLOOR 2TMY3WA | 6A | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,30/Sep | 59 | 11:30,18/Jul | 16
[13 empty] | 6AAUDITORIUMTMY3WA | 6A | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 20:30,02/Feb | 67 | 11:30,18/Jul | 16
[13 empty] | 6AGYMTMY3WA | 6A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 13:30,18/Jan | 42 | 05:30,05/Dec | 11
[13 empty] | 6AKITCHEN CAFETERIATMY3WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 13:30,29/Nov | 56 | 19:30,18/Jul | 13
[13 empty] | 6AFLOOR 1TMY7WA | 6A | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 07:30,22/Sep | 44 | 12:30,08/Aug | 15
[13 empty] | 6AMECHTMY7WA | 6A | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 20:30,15/Oct | 48 | 14:30,08/Aug | 20
[13 empty] | 6AFLOOR 2TMY7WA | 6A | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,21/Sep | 58 | 13:30,08/Aug | 17
[13 empty] | 6AAUDITORIUMTMY7WA | 6A | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 05:30,29/May | 61 | 12:30,08/Aug | 16
[13 empty] | 6AGYMTMY7WA | 6A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 12:30,29/May | 47 | 07:30,24/Jan | 11
[13 empty] | 6AKITCHEN CAFETERIATMY7WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 19:30,08/Nov | 42 | 20:30,08/Aug | 13
[13 empty] | 6AFLOOR 1TMY15WA | 6A | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,15/Apr | 51 | 17:30,04/Jul | 15
[13 empty] | 6AMECHTMY15WA | 6A | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 20:30,15/Oct | 56 | 18:30,04/Jul | 20
[13 empty] | 6AFLOOR 2TMY15WA | 6A | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,30/Sep | 58 | 13:30,08/Aug | 17
[13 empty] | 6AAUDITORIUMTMY15WA | 6A | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 20:30,30/May | 60 | 12:30,08/Aug | 16
[13 empty] | 6AGYMTMY15WA | 6A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 10:30,15/Mar | 42 | 05:30,18/Jan | 11
[13 empty] | 6AKITCHEN CAFETERIATMY15WA | 6A | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 17:30,07/Apr | 53 | 19:30,04/Jul | 14
[13 empty] | 6AFLOOR 1MIN | 6A | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,08/Sep | 45 | 04:30,01/Feb | 17
[13 empty] | 6AMECHMIN | 6A | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 22:30,02/Jul | 49 | 06:30,21/Jan | 23
[13 empty] | 6AFLOOR 2MIN | 6A | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,20/Aug | 45 | 04:30,21/Jan | 18
[13 empty] | 6AAUDITORIUMMIN | 6A | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 18:30,18/Mar | 50 | 07:30,03/Jan | 18
[13 empty] | 6AGYMMIN | 6A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,09/Nov | 49 | 06:30,24/Jan | 12
[13 empty] | 6AKITCHEN CAFETERIAMIN | 6A | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 18:30,23/Sep | 43 | 05:30,01/Feb | 13
[13 empty] | 6AFLOOR 1MAX | 6A | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,09/Apr | 59 | 19:30,18/Jul | 17
[13 empty] | 6AMECHMAX | 6A | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 21:30,30/Oct | 77 | 19:30,18/Jul | 23
[13 empty] | 6AFLOOR 2MAX | 6A | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,23/Apr | 60 | 12:30,18/Jul | 19
[13 empty] | 6AAUDITORIUMMAX | 6A | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 12:30,05/Feb | 65 | 10:30,18/Jul | 17
[13 empty] | 6AGYMMAX | 6A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 15:30,28/Nov | 53 | 19:30,01/Aug | 13
[13 empty] | 6AKITCHEN CAFETERIAMAX | 6A | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 16:30,30/Dec | 60 | 18:30,18/Jul | 16
[13 empty] | 6BLocationFilename | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 6BFLOOR 1TMY7WA | 6B | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 9 | 07:30,01/Jan | 61 | 00:30,05/Apr | 32
[13 empty] | 6BMECHTMY7WA | 6B | People dissatisfied | MECH | TMY7WA | Percentage (%) | 20 | 07:30,19/Jan | 77 | 14:30,05/Apr | 48
[13 empty] | 6BFLOOR 2TMY7WA | 6B | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 7 | 07:30,19/Jan | 61 | 13:30,04/Apr | 34
[13 empty] | 6BAUDITORIUMTMY7WA | 6B | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 10 | 21:30,30/Dec | 78 | 18:30,24/May | 33
[13 empty] | 6BGYMTMY7WA | 6B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 8 | 08:30,19/Jan | 46 | 05:30,06/Apr | 19
[13 empty] | 6BKITCHEN CAFETERIATMY7WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 13 | 07:30,19/Jan | 82 | 13:30,03/Sep | 36
[13 empty] | 6BFLOOR 1TMY3WA | 6B | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 06:30,10/Jun | 36 | 04:30,04/Jan | 14
[13 empty] | 6BMECHTMY3WA | 6B | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 10:30,01/Jun | 47 | 16:30,22/Jul | 19
[13 empty] | 6BFLOOR 2TMY3WA | 6B | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 06:30,02/Sep | 52 | 15:30,25/Jul | 16
[13 empty] | 6BAUDITORIUMTMY3WA | 6B | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 00:30,15/May | 50 | 15:30,18/Jul | 15
[13 empty] | 6BGYMTMY3WA | 6B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 16:30,12/Jun | 55 | 18:30,01/Sep | 12
[13 empty] | 6BKITCHEN CAFETERIATMY3WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 10:30,29/Nov | 38 | 05:30,04/Jan | 11
[13 empty] | 6BFLOOR 1TMY3 | 6B | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,21/May | 41 | 00:30,27/Dec | 14
[13 empty] | 6BMECHTMY3 | 6B | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 09:30,09/Jun | 43 | 01:30,27/Dec | 19
[13 empty] | 6BFLOOR 2TMY3 | 6B | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,02/Jul | 47 | 16:30,08/Aug | 15
[13 empty] | 6BAUDITORIUMTMY3 | 6B | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 10:30,04/May | 48 | 00:30,27/Dec | 15
[13 empty] | 6BGYMTMY3 | 6B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 15:30,06/Jun | 52 | 18:30,21/May | 12
[13 empty] | 6BKITCHEN CAFETERIATMY3 | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 20:30,05/Apr | 39 | 00:30,17/Jan | 11
[13 empty] | 6BFLOOR 1TMY2 | 6B | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 08:30,11/Jun | 44 | 07:30,12/Dec | 14
[13 empty] | 6BMECHTMY2 | 6B | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 00:30,18/Sep | 46 | 06:30,12/Dec | 19
[13 empty] | 6BFLOOR 2TMY2 | 6B | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,31/Aug | 47 | 14:30,26/Jun | 16
[13 empty] | 6BAUDITORIUMTMY2 | 6B | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 10:30,06/Sep | 50 | 03:30,12/Dec | 15
[13 empty] | 6BGYMTMY2 | 6B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 12:30,13/Jan | 49 | 04:30,12/Dec | 12
[13 empty] | 6BKITCHEN CAFETERIATMY2 | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 18:30,12/Mar | 40 | 07:30,12/Dec | 11
[13 empty] | 6BFLOOR 1TMY15WA | 6B | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,13/May | 35 | 03:30,30/Dec | 14
[13 empty] | 6BMECHTMY15WA | 6B | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 23:30,25/Jun | 41 | 14:30,29/Jul | 19
[13 empty] | 6BFLOOR 2TMY15WA | 6B | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,07/Sep | 46 | 14:30,25/Jul | 15
[13 empty] | 6BAUDITORIUMTMY15WA | 6B | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 06:30,04/Sep | 45 | 16:30,24/Jul | 15
[13 empty] | 6BGYMTMY15WA | 6B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 10:30,26/Feb | 52 | 17:30,02/Sep | 12
[13 empty] | 6BKITCHEN CAFETERIATMY15WA | 6B | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 10:30,29/Nov | 37 | 03:30,28/Dec | 11
[13 empty] | 6BFLOOR 1MIN | 6B | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 06:30,22/Jul | 44 | 04:30,06/Dec | 19
[13 empty] | 6BMECHMIN | 6B | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 21:30,28/Jul | 53 | 07:30,17/Feb | 27
[13 empty] | 6BFLOOR 2MIN | 6B | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,22/Jul | 47 | 04:30,17/Feb | 20
[13 empty] | 6BAUDITORIUMMIN | 6B | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 20:30,18/Aug | 50 | 06:30,06/Dec | 20
[13 empty] | 6BGYMMIN | 6B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 13:30,07/Apr | 48 | 23:30,05/Dec | 14
[13 empty] | 6BKITCHEN CAFETERIAMIN | 6B | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 19:30,25/Jun | 43 | 05:30,06/Dec | 14
[13 empty] | 6BFLOOR 1MAX | 6B | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 06:30,13/May | 38 | 16:30,01/Aug | 13
[13 empty] | 6BMECHMAX | 6B | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 09:30,07/May | 52 | 14:30,16/Jul | 18
[13 empty] | 6BFLOOR 2MAX | 6B | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,08/Sep | 50 | 13:30,01/Aug | 15
[13 empty] | 6BAUDITORIUMMAX | 6B | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 12:30,07/Apr | 48 | 17:30,01/Aug | 14
[13 empty] | 6BGYMMAX | 6B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 11:30,01/Mar | 63 | 18:30,03/Sep | 14
[13 empty] | 6BKITCHEN CAFETERIAMAX | 6B | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 20:30,03/Nov | 36 | 19:30,01/Aug | 11
[13 empty] | 7LocationFilename | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 7FLOOR 1TMY2 | 7 | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 07:30,11/Jun | 43 | 03:30,01/Feb | 15
[13 empty] | 7MECHTMY2 | 7 | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 00:30,29/Jul | 47 | 06:30,01/Feb | 21
[13 empty] | 7FLOOR 2TMY2 | 7 | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,15/Sep | 46 | 16:30,11/Jul | 16
[13 empty] | 7AUDITORIUMTMY2 | 7 | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 21:30,21/Sep | 50 | 05:30,08/Feb | 16
[13 empty] | 7GYMTMY2 | 7 | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 12:30,29/Aug | 49 | 05:30,08/Feb | 11
[13 empty] | 7KITCHEN CAFETERIATMY2 | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 18:30,05/Oct | 43 | 05:30,01/Feb | 12
[13 empty] | 7FLOOR 1TMY3 | 7 | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 22:30,04/Jul | 43 | 03:30,20/Dec | 15
[13 empty] | 7MECHTMY3 | 7 | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 13:30,20/Sep | 46 | 06:30,31/Jan | 20
[13 empty] | 7FLOOR 2TMY3 | 7 | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,27/Sep | 52 | 14:30,17/Jul | 16
[13 empty] | 7AUDITORIUMTMY3 | 7 | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 03:30,25/May | 55 | 15:30,17/Jul | 16
[13 empty] | 7GYMTMY3 | 7 | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 12:30,26/Nov | 50 | 05:30,20/Dec | 11
[13 empty] | 7KITCHEN CAFETERIATMY3 | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 18:30,04/May | 40 | 18:30,18/Jul | 12
[13 empty] | 7FLOOR 1TMY3WA | 7 | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,24/May | 44 | 13:30,04/Jul | 14
[13 empty] | 7MECHTMY3WA | 7 | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 00:30,06/May | 44 | 15:30,04/Jul | 18
[13 empty] | 7FLOOR 2TMY3WA | 7 | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 06:30,17/Aug | 55 | 13:30,04/Jul | 15
[13 empty] | 7AUDITORIUMTMY3WA | 7 | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 16:30,19/Nov | 60 | 12:30,04/Jul | 15
[13 empty] | 7GYMTMY3WA | 7 | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 15:30,05/Feb | 43 | 07:30,05/Dec | 10
[13 empty] | 7KITCHEN CAFETERIATMY3WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 17:30,30/Mar | 44 | 19:30,04/Jul | 12
[13 empty] | 7FLOOR 1TMY7WA | 7 | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 06:30,27/May | 41 | 04:30,04/Jan | 15
[13 empty] | 7MECHTMY7WA | 7 | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 08:30,06/Jun | 44 | 04:30,04/Jan | 19
[13 empty] | 7FLOOR 2TMY7WA | 7 | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 06:30,17/Aug | 51 | 16:30,04/Jul | 16
[13 empty] | 7AUDITORIUMTMY7WA | 7 | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 20:30,24/Feb | 50 | 16:30,04/Jul | 16
[13 empty] | 7GYMTMY7WA | 7 | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 13:30,20/Jan | 45 | 06:30,10/Jan | 11
[13 empty] | 7KITCHEN CAFETERIATMY7WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 14:30,19/Nov | 39 | 01:30,01/Feb | 13
[13 empty] | 7FLOOR 1TMY15WA | 7 | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 06:30,27/May | 47 | 10:30,18/Jul | 14
[13 empty] | 7MECHTMY15WA | 7 | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 16:30,24/May | 49 | 13:30,18/Jul | 18
[13 empty] | 7FLOOR 2TMY15WA | 7 | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 06:30,17/Aug | 57 | 12:30,18/Jul | 16
[13 empty] | 7AUDITORIUMTMY15WA | 7 | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 12:30,20/Oct | 67 | 12:30,18/Jul | 15
[13 empty] | 7GYMTMY15WA | 7 | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 10:30,02/Mar | 42 | 01:30,04/Jan | 11
[13 empty] | 7KITCHEN CAFETERIATMY15WA | 7 | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 18:30,02/Nov | 49 | 07:30,18/Jul | 12
[13 empty] | 7FLOOR 1MIN | 7 | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 07:30,18/Aug | 46 | 19:30,17/Jan | 18
[13 empty] | 7MECHMIN | 7 | People dissatisfied | MECH | MIN | Percentage (%) | 5 | 22:30,25/Jul | 50 | 20:30,17/Jan | 25
[13 empty] | 7FLOOR 2MIN | 7 | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,18/Aug | 47 | 07:30,17/Jan | 18
[13 empty] | 7AUDITORIUMMIN | 7 | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 08:30,24/Aug | 53 | 18:30,17/Jan | 19
[13 empty] | 7GYMMIN | 7 | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 11:30,27/Jun | 49 | 18:30,17/Jan | 13
[13 empty] | 7KITCHEN CAFETERIAMIN | 7 | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 16:30,18/May | 45 | 23:30,17/Jan | 13
[13 empty] | 7FLOOR 1MAX | 7 | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 06:30,27/Oct | 54 | 10:30,18/Jul | 15
[13 empty] | 7MECHMAX | 7 | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 08:30,26/Oct | 63 | 13:30,18/Jul | 20
[13 empty] | 7FLOOR 2MAX | 7 | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,30/Sep | 59 | 12:30,18/Jul | 17
[13 empty] | 7AUDITORIUMMAX | 7 | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 13:30,02/Nov | 65 | 11:30,18/Jul | 16
[13 empty] | 7GYMMAX | 7 | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 19:30,10/Apr | 44 | 20:30,18/Jul | 11
[13 empty] | 7KITCHEN CAFETERIAMAX | 7 | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 16:30,03/Mar | 56 | 19:30,18/Jul | 14
[13 empty] | 8LocationFilename | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[13 empty] | 8FLOOR 1TMY2 | 8 | People dissatisfied | FLOOR 1 | TMY2 | Percentage (%) | 5 | 08:30,03/Jun | 49 | 01:30,04/Jan | 18
[13 empty] | 8MECHTMY2 | 8 | People dissatisfied | MECH | TMY2 | Percentage (%) | 5 | 00:30,06/Aug | 56 | 05:30,04/Jan | 24
[13 empty] | 8FLOOR 2TMY2 | 8 | People dissatisfied | FLOOR 2 | TMY2 | Percentage (%) | 5 | 07:30,09/Aug | 49 | 00:30,04/Jan | 19
[13 empty] | 8AUDITORIUMTMY2 | 8 | People dissatisfied | AUDITORIUM | TMY2 | Percentage (%) | 5 | 19:30,07/Aug | 56 | 01:30,04/Jan | 18
[13 empty] | 8GYMTMY2 | 8 | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 16:30,07/Jun | 52 | 20:30,03/Jan | 13
[13 empty] | 8KITCHEN CAFETERIATMY2 | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY2 | Percentage (%) | 5 | 20:30,03/May | 46 | 07:30,17/Jan | 14
[13 empty] | 8FLOOR 1TMY3 | 8 | People dissatisfied | FLOOR 1 | TMY3 | Percentage (%) | 5 | 07:30,20/Aug | 45 | 01:30,01/Mar | 17
[13 empty] | 8MECHTMY3 | 8 | People dissatisfied | MECH | TMY3 | Percentage (%) | 5 | 08:30,11/Jun | 47 | 05:30,01/Mar | 23
[13 empty] | 8FLOOR 2TMY3 | 8 | People dissatisfied | FLOOR 2 | TMY3 | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,12/Jan | 18
[13 empty] | 8AUDITORIUMTMY3 | 8 | People dissatisfied | AUDITORIUM | TMY3 | Percentage (%) | 5 | 17:30,28/Sep | 52 | 03:30,01/Mar | 18
[13 empty] | 8GYMTMY3 | 8 | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 15:30,05/Apr | 50 | 02:30,01/Mar | 12
[13 empty] | 8KITCHEN CAFETERIATMY3 | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY3 | Percentage (%) | 5 | 19:30,20/Apr | 45 | 05:30,01/Mar | 14
[13 empty] | 8FLOOR 1TMY3WA | 8 | People dissatisfied | FLOOR 1 | TMY3WA | Percentage (%) | 5 | 07:30,18/May | 43 | 21:30,05/Dec | 15
[13 empty] | 8MECHTMY3WA | 8 | People dissatisfied | MECH | TMY3WA | Percentage (%) | 5 | 00:30,29/May | 45 | 23:30,05/Dec | 21
[13 empty] | 8FLOOR 2TMY3WA | 8 | People dissatisfied | FLOOR 2 | TMY3WA | Percentage (%) | 5 | 07:30,27/Aug | 51 | 15:30,19/Jun | 17
[13 empty] | 8AUDITORIUMTMY3WA | 8 | People dissatisfied | AUDITORIUM | TMY3WA | Percentage (%) | 5 | 13:30,20/Apr | 49 | 04:30,06/Dec | 16
[13 empty] | 8GYMTMY3WA | 8 | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 12:30,01/Apr | 48 | 19:30,13/May | 12
[13 empty] | 8KITCHEN CAFETERIATMY3WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY3WA | Percentage (%) | 5 | 16:30,01/Oct | 39 | 02:30,06/Dec | 12
[13 empty] | 8FLOOR 1TMY7WA | 8 | People dissatisfied | FLOOR 1 | TMY7WA | Percentage (%) | 5 | 07:30,20/Aug | 44 | 03:30,28/Jan | 16
[13 empty] | 8MECHTMY7WA | 8 | People dissatisfied | MECH | TMY7WA | Percentage (%) | 5 | 00:30,01/Jul | 48 | 05:30,28/Jan | 22
[13 empty] | 8FLOOR 2TMY7WA | 8 | People dissatisfied | FLOOR 2 | TMY7WA | Percentage (%) | 5 | 07:30,19/Aug | 47 | 03:30,26/Jan | 17
[13 empty] | 8AUDITORIUMTMY7WA | 8 | People dissatisfied | AUDITORIUM | TMY7WA | Percentage (%) | 5 | 19:30,18/Mar | 48 | 06:30,27/Jan | 17
[13 empty] | 8GYMTMY7WA | 8 | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 16:30,09/Nov | 51 | 19:30,26/May | 12
[13 empty] | 8KITCHEN CAFETERIATMY7WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY7WA | Percentage (%) | 5 | 16:30,23/Sep | 43 | 05:30,27/Jan | 13
[13 empty] | 8FLOOR 1TMY15WA | 8 | People dissatisfied | FLOOR 1 | TMY15WA | Percentage (%) | 5 | 07:30,11/Aug | 40 | 07:30,21/Feb | 16
[13 empty] | 8MECHTMY15WA | 8 | People dissatisfied | MECH | TMY15WA | Percentage (%) | 5 | 01:30,14/Aug | 43 | 07:30,21/Feb | 22
[13 empty] | 8FLOOR 2TMY15WA | 8 | People dissatisfied | FLOOR 2 | TMY15WA | Percentage (%) | 5 | 07:30,01/Sep | 51 | 15:30,19/Jun | 18
[13 empty] | 8AUDITORIUMTMY15WA | 8 | People dissatisfied | AUDITORIUM | TMY15WA | Percentage (%) | 5 | 15:30,21/Apr | 48 | 15:30,20/Jun | 17
[13 empty] | 8GYMTMY15WA | 8 | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,02/Oct | 47 | 03:30,15/Feb | 12
[13 empty] | 8KITCHEN CAFETERIATMY15WA | 8 | People dissatisfied | KITCHEN CAFETERIA | TMY15WA | Percentage (%) | 5 | 17:30,15/Apr | 39 | 22:30,02/Jan | 13
[13 empty] | 8FLOOR 1MIN | 8 | People dissatisfied | FLOOR 1 | MIN | Percentage (%) | 5 | 15:30,16/Jul | 50 | 04:30,18/Jan | 22
[13 empty] | 8MECHMIN | 8 | People dissatisfied | MECH | MIN | Percentage (%) | 6 | 19:30,17/Jun | 57 | 06:30,18/Jan | 30
[13 empty] | 8FLOOR 2MIN | 8 | People dissatisfied | FLOOR 2 | MIN | Percentage (%) | 5 | 07:30,02/Jul | 50 | 04:30,11/Jan | 22
[13 empty] | 8AUDITORIUMMIN | 8 | People dissatisfied | AUDITORIUM | MIN | Percentage (%) | 5 | 21:30,23/Jul | 58 | 04:30,11/Jan | 23
[13 empty] | 8GYMMIN | 8 | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 21:30,07/Jun | 53 | 05:30,18/Jan | 15
[13 empty] | 8KITCHEN CAFETERIAMIN | 8 | People dissatisfied | KITCHEN CAFETERIA | MIN | Percentage (%) | 5 | 15:30,27/Apr | 47 | 05:30,12/Jan | 17
[13 empty] | 8FLOOR 1MAX | 8 | People dissatisfied | FLOOR 1 | MAX | Percentage (%) | 5 | 07:30,01/Sep | 39 | 20:30,27/Jun | 15
[13 empty] | 8MECHMAX | 8 | People dissatisfied | MECH | MAX | Percentage (%) | 5 | 10:30,17/Sep | 43 | 16:30,28/Jun | 21
[13 empty] | 8FLOOR 2MAX | 8 | People dissatisfied | FLOOR 2 | MAX | Percentage (%) | 5 | 07:30,06/Sep | 51 | 15:30,20/Jun | 17
[13 empty] | 8AUDITORIUMMAX | 8 | People dissatisfied | AUDITORIUM | MAX | Percentage (%) | 5 | 19:30,23/Feb | 49 | 18:30,27/Jun | 16
[13 empty] | 8GYMMAX | 8 | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 14:30,17/Nov | 61 | 19:30,26/May | 13
[13 empty] | 8KITCHEN CAFETERIAMAX | 8 | People dissatisfied | KITCHEN CAFETERIA | MAX | Percentage (%) | 5 | 18:30,14/Oct | 41 | 22:30,27/Jun | 12

## 4s Summary of Results
| Building Area (ft2): | 211975
1A - Miami | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 645958 | 4721126 | 2555342 | 175825 | 1078516 | 2274458 | 0 | 301349 | 938047 | 96624 | 2350761 | 12787245 | 60.3243 | max EUI | max EUI
| TMY3 DOE | 644623 | 4976729 | 2555342 | 178641 | 1078516 | 2302891 | 0 | 317664 | 938047 | 96624 | 2350761 | 13089077 | 61.7482 | 69.7339 | 66.6658
| TMY3 WA | 331737 | 6095926 | 2555342 | 180906 | 1078516 | 2465286 | 0 | 389102 | 938047 | 96624 | 2350761 | 14131486 | 66.6658 | min EUI | min EUI
| TMY7 WA | 496756 | 5418204 | 2555342 | 182207 | 1078516 | 2372017 | 0 | 345843 | 938047 | 96624 | 2350761 | 13483556 | 63.6092 | 58.6219 | 60.3243
| TMY15 WA | 453669 | 5657474 | 2555342 | 181525 | 1078516 | 2421417 | 0 | 361115 | 938047 | 96624 | 2350761 | 13743729 | 64.8366 | variance | variance
| XMY Min WA | 1737749 | 3488232 | 2555342 | 183602 | 1078516 | 2125622 | 0 | 222653 | 938047 | 96624 | 2350761 | 12426387 | 58.6219 | 18% | 10.27%
| XMY Max WA | 258989 | 6685013 | 2555342 | 178359 | 1078516 | 2564241 | 0 | 426703 | 938047 | 96624 | 2350761 | 14781834 | 69.7339
2A - Houston | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1833175 | 3697739 | 2555342 | 177640 | 1078516 | 2109562 | 0 | 236026 | 938047 | 96624 | 2350761 | 12722671 | 60.0197 | max EUI | max EUI
| TMY3 DOE | 1694625 | 3816957 | 2555342 | 179554 | 1078516 | 2126875 | 0 | 243636 | 938047 | 96624 | 2350761 | 12730176 | 60.0551 | 64.8832 | 62.2093
| TMY3 WA | 1053519 | 4749569 | 2555342 | 186049 | 1078516 | 2225996 | 0 | 303164 | 938047 | 96624 | 2350761 | 13186826 | 62.2093 | min EUI | min EUI
| TMY7 WA | 1283384 | 4332749 | 2555342 | 186368 | 1078516 | 2181262 | 0 | 276558 | 938047 | 96624 | 2350761 | 12928850 | 60.9923 | 58.3514 | 58.3514
| TMY15 WA | 926935 | 4270474 | 2555342 | 186368 | 1078516 | 2044145 | 0 | 272583 | 938047 | 96624 | 2350761 | 12369034 | 58.3514 | variance | variance
| XMY Min WA | 4096646 | 2530813 | 2555342 | 195846 | 1078516 | 2100245 | 0 | 161541 | 938047 | 96624 | 2350761 | 13753620 | 64.8832 | 10.88% | 6.424%
| XMY Max WA | 532076 | 5594304 | 2555342 | 183590 | 1078516 | 2327043 | 0 | 357083 | 938047 | 96624 | 2350761 | 13662625 | 64.4539
2B - Phoenix | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1459159 | 3809420 | 2555342 | 175394 | 1078516 | 2282048 | 0 | 243154 | 938047 | 96624 | 2350761 | 12637704 | 59.6188 | max EUI | max EUI
| TMY3 DOE | 1225335 | 4164876 | 2555342 | 177114 | 1078516 | 2348483 | 0 | 265843 | 938047 | 96624 | 2350761 | 12850180 | 60.6212 | 63.763 | 60.9079
| TMY3 WA | 1169019 | 4293788 | 2555342 | 181625 | 1078516 | 2323925 | 0 | 274071 | 938047 | 96624 | 2350761 | 12910957 | 60.9079 | min EUI | min EUI
| TMY7 WA | 1310243 | 3980590 | 2555342 | 180843 | 1078516 | 2264290 | 0 | 254080 | 938047 | 96624 | 2350761 | 12658575 | 59.7173 | 59.4353 | 59.6188
| TMY15 WA | 1310793 | 4168209 | 2555342 | 181125 | 1078516 | 2304604 | 0 | 266056 | 938047 | 96624 | 2350761 | 12899316 | 60.853 | variance | variance
| XMY Min WA | 3054630 | 2433873 | 2555342 | 181419 | 1078516 | 2104991 | 0 | 155353 | 938047 | 96624 | 2350761 | 12598795 | 59.4353 | 7.139% | 2.126%
| XMY Max WA | 775892 | 5121083 | 2555342 | 179385 | 1078516 | 2444394 | 0 | 326878 | 938047 | 96624 | 2350761 | 13516161 | 63.763
3A - Atlanta | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 3188397 | 2414318 | 2555342 | 177771 | 1078516 | 2046925 | 0 | 154105 | 938047 | 96624 | 2350761 | 12650045 | 59.6771 | max EUI | max EUI
| TMY3 DOE | 2934486 | 2612169 | 2555342 | 180756 | 1078516 | 2066218 | 0 | 166734 | 938047 | 96624 | 2350761 | 12628892 | 59.5773 | 66.298 | 59.6771
| TMY3 WA | 2055064 | 3158383 | 2555342 | 188858 | 1078516 | 2081351 | 0 | 201599 | 938047 | 96624 | 2350761 | 12353784 | 58.2794 | min EUI | min EUI
| TMY7 WA | 2531021 | 2933158 | 2555342 | 189208 | 1078516 | 2083671 | 0 | 187223 | 938047 | 96624 | 2350761 | 12592810 | 59.4071 | 57.2265 | 58.2794
| TMY15 WA | 2233339 | 3062917 | 2555342 | 188094 | 1078516 | 2088007 | 0 | 195505 | 938047 | 96624 | 2350761 | 12436391 | 58.6691 | variance | variance
| XMY Min WA | 5681527 | 1472540 | 2555342 | 187506 | 1078516 | 1949421 | 0 | 93992 | 938047 | 96624 | 2350761 | 14053515 | 66.298 | 15.23% | 2.346%
| XMY Max WA | 1071919 | 3818620 | 2555342 | 189433 | 1078516 | 2138334 | 0 | 243742 | 938047 | 96624 | 2350761 | 12130577 | 57.2265
3B - Las Vegas | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 2059854 | 3004542 | 2555342 | 174724 | 1078516 | 2164269 | 0 | 191779 | 938047 | 96624 | 2350761 | 12263697 | 57.8544 | max EUI | max EUI
| TMY3 DOE | 2073730 | 3104343 | 2555342 | 177559 | 1078516 | 2184153 | 0 | 198149 | 938047 | 96624 | 2350761 | 12406463 | 58.528 | 62.3471 | 59.2807
| TMY3 WA | 1949076 | 3351022 | 2555342 | 180956 | 1078516 | 2202550 | 0 | 213895 | 938047 | 96624 | 2350761 | 12566028 | 59.2807 | min EUI | min EUI
| TMY7 WA | 2033005 | 3144086 | 2555342 | 180831 | 1078516 | 2166478 | 0 | 200686 | 938047 | 96624 | 2350761 | 12393615 | 58.4673 | 57.8544 | 57.8544
| TMY15 WA | 2069311 | 3187971 | 2555342 | 180906 | 1078516 | 2181582 | 0 | 203487 | 938047 | 96624 | 2350761 | 12491786 | 58.9305 | variance | variance
| XMY Min WA | 4491584 | 1691268 | 2555342 | 180599 | 1078516 | 2076094 | 0 | 107953 | 938047 | 96624 | 2350761 | 13216027 | 62.3471 | 7.676% | 2.437%
| XMY Max WA | 1282731 | 4169456 | 2555342 | 179980 | 1078516 | 2279738 | 0 | 266135 | 938047 | 96624 | 2350761 | 12846569 | 60.6042
3C - San Francisco | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 2933725 | 885563 | 2555342 | 179911 | 1078516 | 1733694 | 0 | 56525 | 938047 | 96624 | 2350761 | 10457947 | 49.3358 | max EUI | max EUI
| TMY3 DOE | 2631319 | 946801 | 2555342 | 181650 | 1078516 | 1722018 | 0 | 60434 | 938047 | 96624 | 2350761 | 10210751 | 48.1696 | 53.4308 | 49.3358
| TMY3 WA | 2130840 | 1163677 | 2555342 | 185980 | 1078516 | 1739720 | 0 | 74277 | 938047 | 96624 | 2350761 | 9963023 | 47.0009 | min EUI | min EUI
| TMY7 WA | 2745489 | 848010 | 2555342 | 188245 | 1078516 | 1704773 | 0 | 54128 | 938047 | 96624 | 2350761 | 10209174 | 48.1622 | 47.0009 | 47.0009
| TMY15 WA | 2491758 | 999309 | 2555342 | 187331 | 1078516 | 1723821 | 0 | 63786 | 938047 | 96624 | 2350761 | 10134534 | 47.81 | variance | variance
| XMY Min WA | 4088958 | 583928 | 2555342 | 183577 | 1078516 | 1763727 | 0 | 37272 | 938047 | 96624 | 2350761 | 11325991 | 53.4308 | 13.35% | 4.847%
| XMY Max WA | 1712669 | 1535686 | 2555342 | 183202 | 1078516 | 1817254 | 0 | 98022 | 938047 | 96624 | 2350761 | 10015362 | 47.2478
4A - Baltimore | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5919550 | 1654369 | 2555342 | 182245 | 1078516 | 2186666 | 18408 | 105598 | 938047 | 96624 | 2350761 | 14735365 | 69.5146 | max EUI | max EUI
| TMY3 DOE | 5436856 | 1729698 | 2555342 | 182689 | 1078516 | 2174581 | 17079 | 110406 | 938047 | 96624 | 2350761 | 14319838 | 67.5544 | 87.6121 | 69.5146
| TMY3 WA | 3705315 | 2245823 | 2555342 | 190372 | 1078516 | 2160796 | 12389 | 143350 | 938047 | 96624 | 2350761 | 13126574 | 61.9251 | min EUI | min EUI
| TMY7 WA | 4421930 | 2015371 | 2555342 | 191116 | 1078516 | 2161343 | 14423 | 128641 | 938047 | 96624 | 2350761 | 13601353 | 64.1649 | 57.4037 | 61.9251
| TMY15 WA | 3925067 | 2184180 | 2555342 | 189302 | 1078516 | 2175061 | 13000 | 139416 | 938047 | 96624 | 2350761 | 13294555 | 62.7176 | variance | variance
| XMY Min WA | 10525529 | 825695 | 2555342 | 193519 | 1078516 | 2275313 | 30289 | 52704 | 938047 | 96624 | 2350761 | 18571578 | 87.6121 | 44.72% | 11.23%
| XMY Max WA | 1787979 | 3169444 | 2555342 | 191273 | 1078516 | 2141913 | 6708 | 202305 | 938047 | 96624 | 2350761 | 12168151 | 57.4037
4B - Albuquerque | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5159009 | 1417906 | 2555342 | 177490 | 1078516 | 2150240 | 16000 | 90505 | 938047 | 96624 | 2350761 | 13679679 | 64.5344 | max EUI | max EUI
| TMY3 DOE | 4824900 | 1439692 | 2555342 | 178747 | 1078516 | 2135065 | 15004 | 91895 | 938047 | 96624 | 2350761 | 13353832 | 62.9972 | 84.8249 | 64.9678
| TMY3 WA | 4158060 | 1774565 | 2555342 | 180756 | 1078516 | 2178085 | 13678 | 113270 | 938047 | 96624 | 2350761 | 13086943 | 61.7381 | min EUI | min EUI
| TMY7 WA | 4981003 | 1620859 | 2555342 | 181037 | 1078516 | 2200692 | 15970 | 103459 | 938047 | 96624 | 2350761 | 13771549 | 64.9678 | 58.9233 | 61.7381
| TMY15 WA | 4826777 | 1733041 | 2555342 | 181043 | 1078516 | 2199100 | 15529 | 110620 | 938047 | 96624 | 2350761 | 13734639 | 64.7937 | variance | variance
| XMY Min WA | 9982598 | 778825 | 2555342 | 181150 | 1078516 | 2290972 | 28980 | 49712 | 938047 | 96624 | 2350761 | 17980766 | 84.8249 | 41.12% | 5.127%
| XMY Max WA | 3038697 | 2285574 | 2555342 | 179748 | 1078516 | 2161505 | 10327 | 145888 | 938047 | 96624 | 2350761 | 12490268 | 58.9233
4C - Portland | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5131418 | 805120 | 2555342 | 184760 | 1078516 | 1980922 | 16022 | 51391 | 938047 | 96624 | 2350761 | 12838162 | 60.5645 | max EUI | max EUI
| TMY3 DOE | 4821955 | 854417 | 2555342 | 186856 | 1078516 | 1975891 | 15217 | 54537 | 938047 | 96624 | 2350761 | 12577402 | 59.3344 | 85.5237 | 63.3027
| TMY3 WA | 4409855 | 1065047 | 2555342 | 199050 | 1078516 | 1988226 | 14331 | 67982 | 938047 | 96624 | 2350761 | 12413020 | 58.5589 | min EUI | min EUI
| TMY7 WA | 5325780 | 1077345 | 2555342 | 195840 | 1078516 | 2065684 | 16638 | 68767 | 938047 | 96624 | 2350761 | 13418583 | 63.3027 | 55.1433 | 58.5589
| TMY15 WA | 4848669 | 1096597 | 2555342 | 196879 | 1078516 | 2026946 | 15509 | 69996 | 938047 | 96624 | 2350761 | 12923125 | 60.9653 | variance | variance
| XMY Min WA | 10601774 | 375803 | 2555342 | 194088 | 1078516 | 2234715 | 29980 | 23987 | 938047 | 96624 | 2350761 | 18128876 | 85.5237 | 51.2% | 7.995%
| XMY Max WA | 2931463 | 1761744 | 2555342 | 199563 | 1078516 | 2005015 | 10234 | 112452 | 938047 | 96624 | 2350761 | 11689000 | 55.1433
5A - Chicago | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 8403421 | 1271474 | 2555342 | 181694 | 1078516 | 2237923 | 26457 | 81158 | 938047 | 96624 | 2350761 | 16870656 | 79.588 | max EUI | max EUI
| TMY3 DOE | 8179074 | 1339139 | 2555342 | 183540 | 1078516 | 2240615 | 25989 | 85477 | 938047 | 96624 | 2350761 | 16722363 | 78.8884 | 106.1866 | 79.588
| TMY3 WA | 5448217 | 1610657 | 2555342 | 191961 | 1078516 | 2141966 | 18571 | 102808 | 938047 | 96624 | 2350761 | 14182709 | 66.9075 | min EUI | min EUI
| TMY7 WA | 6922294 | 1426336 | 2555342 | 190991 | 1078516 | 2200536 | 22771 | 91043 | 938047 | 96624 | 2350761 | 15522500 | 73.228 | 59.8156 | 66.9075
| TMY15 WA | 6335906 | 1548204 | 2555342 | 190691 | 1078516 | 2189323 | 20875 | 98822 | 938047 | 96624 | 2350761 | 15052350 | 71.01 | variance | variance
| XMY Min WA | 14674563 | 524311 | 2555342 | 188582 | 1078516 | 2376482 | 42972 | 33467 | 938047 | 96624 | 2350761 | 22508906 | 106.1866 | 58.78% | 16.07%
| XMY Max WA | 3340899 | 2201721 | 2555342 | 193406 | 1078516 | 2122189 | 12135 | 140535 | 938047 | 96624 | 2350761 | 12679414 | 59.8156
5B - Boulder | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 7313102 | 1096814 | 2555342 | 179448 | 1078516 | 2179944 | 23730 | 70009 | 938047 | 96624 | 2350761 | 15531576 | 73.2708 | max EUI | max EUI
| TMY3 DOE | 6910784 | 1094066 | 2555342 | 181775 | 1078516 | 2170465 | 22666 | 69834 | 938047 | 96624 | 2350761 | 15118119 | 71.3203 | 120.0066 | 77.3982
| TMY3 WA | 8128743 | 969920 | 2555342 | 182708 | 1078516 | 2243553 | 26730 | 61910 | 938047 | 96624 | 2350761 | 16282093 | 76.8114 | min EUI | min EUI
| TMY7 WA | 8221505 | 993236 | 2555342 | 182795 | 1078516 | 2250265 | 26763 | 63398 | 938047 | 96624 | 2350761 | 16406491 | 77.3982 | 63.8631 | 71.3203
| TMY15 WA | 7743357 | 1041494 | 2555342 | 182320 | 1078516 | 2248595 | 25472 | 66478 | 938047 | 96624 | 2350761 | 15976245 | 75.3685 | variance | variance
| XMY Min WA | 17580297 | 399685 | 2555342 | 185905 | 1078516 | 2527211 | 51268 | 25512 | 938047 | 96624 | 2350761 | 25438407 | 120.0066 | 78.72% | 8.522%
| XMY Max WA | 4919769 | 1501483 | 2555342 | 180405 | 1078516 | 2154288 | 17067 | 95839 | 938047 | 96624 | 2350761 | 13537380 | 63.8631
5C - Vancouver | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
[15 empty] | max EUI | max EUI
| CWEC | 6158971 | 475365 | 2555342 | 197873 | 1078516 | 1973091 | 19313 | 30342 | 938047 | 96624 | 2350761 | 13523484 | 63.7975 | 86.4619 | 64.5594
| TMY3 WA | 4944220 | 623999 | 2555342 | 198124 | 1078516 | 1912245 | 16085 | 39830 | 938047 | 96624 | 2350761 | 12403032 | 58.5118 | min EUI | min EUI
| TMY7 WA | 6349647 | 441983 | 2555342 | 200013 | 1078516 | 1976750 | 19845 | 28212 | 938047 | 96624 | 2350761 | 13684979 | 64.5594 | 54.7913 | 58.1196
| TMY15 WA | 5159097 | 475725 | 2555342 | 199782 | 1078516 | 1769960 | 16451 | 30365 | 938047 | 96624 | 2350761 | 12319909 | 58.1196 | variance | variance
| XMY Min WA | 10984464 | 267904 | 2555342 | 194764 | 1078516 | 2164031 | 30959 | 17100 | 938047 | 96624 | 2350761 | 18327751 | 86.4619 | 49.64% | 10.09%
| XMY Max WA | 3977186 | 814293 | 2555342 | 201408 | 1078516 | 1887241 | 13749 | 51976 | 938047 | 96624 | 2350761 | 11614382 | 54.7913
6A - Minneapolis | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 10731799 | 1138300 | 2555342 | 182007 | 1078516 | 2318080 | 32999 | 72657 | 938047 | 96624 | 2350761 | 19144371 | 90.3143 | max EUI | max EUI
| TMY3 DOE | 10354618 | 1126987 | 2555342 | 184378 | 1078516 | 2310918 | 32706 | 71935 | 938047 | 96624 | 2350761 | 18750071 | 88.4542 | 124.7117 | 90.3143
| TMY3 WA | 6872606 | 1530370 | 2555342 | 192587 | 1078516 | 2216719 | 23259 | 97683 | 938047 | 96624 | 2350761 | 15601753 | 73.6019 | min EUI | min EUI
| TMY7 WA | 9533637 | 1271064 | 2555342 | 192030 | 1078516 | 2306344 | 30667 | 81132 | 938047 | 96624 | 2350761 | 18083403 | 85.3091 | 67.2144 | 73.6019
| TMY15 WA | 8148369 | 1457799 | 2555342 | 192430 | 1078516 | 2266821 | 26509 | 93051 | 938047 | 96624 | 2350761 | 16853508 | 79.5071 | variance | variance
| XMY Min WA | 18480732 | 486815 | 2555342 | 191010 | 1078516 | 2523997 | 53607 | 31073 | 938047 | 96624 | 2350761 | 26435763 | 124.7117 | 65% | 18.89%
| XMY Max WA | 4669995 | 2309922 | 2555342 | 193137 | 1078516 | 2242056 | 16681 | 147442 | 938047 | 96624 | 2350761 | 14247762 | 67.2144
6B - Helena | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 10060920 | 757774 | 2555342 | 181619 | 1078516 | 2226401 | 32647 | 48369 | 938047 | 96624 | 2350761 | 17976259 | 84.8037 | max EUI | max EUI
| TMY3 DOE | 9663510 | 747971 | 2555342 | 183183 | 1078516 | 2216233 | 31687 | 47743 | 938047 | 96624 | 2350761 | 17558856 | 82.8346 | 133.8566 | 84.8037
| TMY3 WA | 8636574 | 1045854 | 2555342 | 187769 | 1078516 | 2273738 | 29592 | 66757 | 938047 | 96624 | 2350761 | 16908813 | 79.768 | min EUI | min EUI
| TMY7 WA | 384379 | 5889196 | 2555342 | 184134 | 1078516 | 2341222 | 1835 | 375906 | 938047 | 96624 | 2350761 | 13845201 | 65.3153 | 65.3153 | 65.3153
| TMY15 WA | 9238993 | 919374 | 2555342 | 187976 | 1078516 | 2271929 | 31334 | 58683 | 938047 | 96624 | 2350761 | 17376818 | 81.9758 | variance | variance
| XMY Min WA | 20503422 | 327336 | 2555342 | 188683 | 1078516 | 2604521 | 60866 | 20894 | 938047 | 96624 | 2350761 | 28374251 | 133.8566 | 82.74% | 23.53%
| XMY Max WA | 6351678 | 1429423 | 2555342 | 185698 | 1078516 | 2195889 | 22606 | 91240 | 938047 | 96624 | 2350761 | 14945063 | 70.5039
7 - Duluth | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 13245915 | 632297 | 2555342 | 181744 | 1078516 | 2328962 | 40435 | 40359 | 938047 | 96624 | 2350761 | 21138241 | 99.7204 | max EUI | max EUI
| TMY3 DOE | 12567043 | 672743 | 2555342 | 184084 | 1078516 | 2305416 | 39026 | 42941 | 938047 | 96624 | 2350761 | 20479782 | 96.6141 | 130.5291 | 99.7204
| TMY3 WA | 8027763 | 1127046 | 2555342 | 195014 | 1078516 | 2198144 | 27024 | 71939 | 938047 | 96624 | 2350761 | 16315459 | 76.9688 | min EUI | min EUI
| TMY7 WA | 10466150 | 957234 | 2555342 | 194789 | 1078516 | 2288738 | 33663 | 61100 | 938047 | 96624 | 2350761 | 18670203 | 88.0774 | 68.7809 | 76.9688
| TMY15 WA | 8957747 | 1029141 | 2555342 | 193819 | 1078516 | 2222187 | 29426 | 65690 | 938047 | 96624 | 2350761 | 17166539 | 80.9838 | variance | variance
| XMY Min WA | 19840746 | 355671 | 2555342 | 192124 | 1078516 | 2531609 | 57520 | 22702 | 938047 | 96624 | 2350761 | 27668901 | 130.5291 | 63.91% | 23.55%
| XMY Max WA | 5733166 | 1683490 | 2555342 | 197235 | 1078516 | 2169602 | 20346 | 107457 | 938047 | 96624 | 2350761 | 14579825 | 68.7809
8 - Fairbanks | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 20567520 | 361426 | 2555342 | 202309 | 1078516 | 2494464 | 61588 | 23070 | 938047 | 96624 | 2350761 | 28378906 | 133.8786 | max EUI | max EUI
| TMY3 DOE | 18587447 | 398704 | 2555342 | 203529 | 1078516 | 2452966 | 57131 | 25449 | 938047 | 96624 | 2350761 | 26393755 | 124.5135 | 176.2182 | 133.8786
| TMY3 WA | 13594395 | 624964 | 2555342 | 205713 | 1078516 | 2344865 | 45067 | 39891 | 938047 | 96624 | 2350761 | 21523424 | 101.5376 | min EUI | min EUI
| TMY7 WA | 16768533 | 464774 | 2555342 | 205813 | 1078516 | 2429658 | 53731 | 29666 | 938047 | 96624 | 2350761 | 24620704 | 116.1491 | 86.3903 | 101.5376
| TMY15 WA | 15496793 | 569789 | 2555342 | 206163 | 1078516 | 2397926 | 50011 | 36370 | 938047 | 96624 | 2350761 | 23425581 | 110.5111 | variance | variance
| XMY Min WA | 29378988 | 211116 | 2555342 | 208685 | 1078516 | 2788505 | 84548 | 13475 | 938047 | 96624 | 2350761 | 37353846 | 176.2182 | 72.14% | 25.97%
| XMY Max WA | 10198184 | 885220 | 2555342 | 205175 | 1078516 | 2262649 | 36330 | 56503 | 938047 | 96624 | 2350761 | 18312590 | 86.3903
1A - Miami
2A - Houston
2B - Phoenix
3A - Atlanta
3B - Las Vegas
3C - San Francisco
4A - Baltimore
4B - Albuquerque
4C - Portland
5A - Chicago
5B - Boulder
5C - Vancouver
6A - Minneapolis
6B - Helena
7 - Duluth
8 - Fairbanks

## 4s Additional Indicators
[16 empty] | Predicted Percentage Dissatisfied(21C ZONING) | [9 empty] | Peak Heating Load | [9 empty] | Peak Cooling Load
Climate Zone | Climate File | ADMIN | LEARNING 1 | LEARNING 2 | PERFORMANCE | LEARNING 4 | LEARNING 3 | FOOD PREP | GYM | Unmet Hours (Cooling) | UH Compliance | Peak Heating Load | Peak Cooling Load | Overheating Risk |  | Climate | [9 empty] | Climate | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | Climate | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY15WA | 27 | 31 | 21 | 22 | 24 | 26 | 33 | 27 | 220 | 220 | 3988641 | 2568606 |  |  |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 1A | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 3988641 | 12:00, January | 3988641 | 12:00, January | 3988641 | 1A | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 193823 | 04:30, May | 2568606 | 13:30, September | 1037808
1A | TMY7WA | 25 | 29 | 20 | 21 | 23 | 24 | 32 | 25 | 225 | 225 |  |  |  | 1AADMINTMY15WA | 1A | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,11/Jan | 57 | 08:30,11/Jul | 27 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY3WA | 29 | 33 | 23 | 23 | 26 | 28 | 34 | 28 | 274 | 274 |  |  |  | 1ALEARNING 1TMY15WA | 1A | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,05/Mar | 64 | 08:30,17/Jul | 31 | 2A | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 4129798 | 12:00, January | 4129798 | 12:00, January | 4129798 | 2A | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 154285 | 04:30, May | 2359777 | 13:30, September | 885999
1A | TMY3 | 23 | 27 | 19 | 20 | 21 | 23 | 31 | 25 | 232 | 232 |  |  |  | 1ALEARNING 2TMY15WA | 1A | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 06:30,11/Jan | 52 | 13:30,28/Aug | 21 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | TMY2 | 23 | 26 | 18 | 19 | 21 | 22 | 31 | 24 | 267 | 267 |  |  |  | 1APERFORMANCETMY15WA | 1A | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 19:30,27/Dec | 54 | 23:30,17/Jul | 22 | 2B | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 3651144 | 12:00, January | 3651144 | 12:00, January | 3651144 | 2B | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 223845 | 04:30, May | 2933947 | 13:30, September | 1310614
1A | MIN | 18 | 21 | 15 | 15 | 17 | 18 | 25 | 20 | 313 | 313 |  |  |  | 1ALEARNING 4TMY15WA | 1A | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 06:30,11/Jan | 51 | 08:30,29/Aug | 24 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
1A | MAX | 32 | 36 | 26 | 25 | 28 | 30 | 35 | 30 | 155 | 155 |  |  |  | 1ALEARNING 3TMY15WA | 1A | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 06:30,11/Jan | 56 | 19:30,14/Sep | 26 | 3A | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 4399384 | 12:00, January | 4399384 | 12:00, January | 4399384 | 3A | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 140171 | 04:30, May | 2052857 | 13:30, September | 782213
2A | TMY7WA | 19 | 23 | 16 | 15 | 17 | 18 | 29 | 21 | 197 | 197 | 4129798 | 2359777 |  | 1AFOOD PREPTMY15WA | 1A | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 6 | 08:30,04/Jan | 48 | 12:30,11/Jul | 33 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY3WA | 21 | 24 | 17 | 16 | 19 | 20 | 30 | 22 | 197 | 197 |  |  |  | 1AGYMTMY15WA | 1A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 14:30,04/Jan | 46 | 11:30,08/May | 27 | 3B | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 3934210 | 12:00, January | 3934210 | 12:00, January | 3934210 | 3B | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 197704 | 04:30, May | 2476394 | 13:30, September | 1113350
2A | TMY3 | 18 | 22 | 15 | 15 | 17 | 18 | 28 | 20 | 266 | 266 |  |  |  | 1AADMINTMY7WA | 1A | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 03:30,06/Jan | 57 | 08:30,18/Jul | 25 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY2 | 18 | 21 | 15 | 14 | 16 | 17 | 28 | 20 | 253 | 253 |  |  |  | 1ALEARNING 1TMY7WA | 1A | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,04/Jan | 65 | 09:30,05/Sep | 29 | 3C | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 3542153 | 12:00, January | 3542153 | 12:00, January | 3542153 | 3C | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 75818 | 07:30, August | 1819953 | 13:30, September | 552260
2A | TMY15WA | 19 | 23 | 17 | 16 | 18 | 20 | 29 | 21 | 255 | 255 |  |  |  | 1ALEARNING 2TMY7WA | 1A | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 06:30,28/Jan | 53 | 13:30,04/Sep | 20 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | MIN | 17 | 20 | 15 | 13 | 16 | 16 | 22 | 18 | 363 | 363 |  |  |  | 1APERFORMANCETMY7WA | 1A | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 19:30,21/Dec | 55 | 21:30,18/Jul | 21 | 4A | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 4495864 | 12:00, January | 4495864 | 12:00, January | 4495864 | 4A | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 141160 | 04:30, May | 2141118 | 13:30, September | 788778
2A | MAX | 24 | 28 | 20 | 20 | 22 | 23 | 33 | 25 | 142 | 142 |  |  |  | 1ALEARNING 4TMY7WA | 1A | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 05:30,15/Feb | 53 | 10:30,05/Sep | 23 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY15WA | 17 | 20 | 15 | 13 | 15 | 17 | 22 | 17 | 156 | 156 | 3651144 | 2933947 |  | 1ALEARNING 3TMY7WA | 1A | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 00:30,15/Feb | 56 | 19:30,08/Sep | 24 | 4B | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 4290498 | 12:00, January | 4290498 | 12:00, January | 4290498 | 4B | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 127843 | 04:30, May | 1920707 | 13:30, September | 681295
2B | TMY7WA | 16 | 19 | 15 | 12 | 14 | 16 | 22 | 17 | 144 | 144 |  |  |  | 1AFOOD PREPTMY7WA | 1A | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 7 | 07:30,12/Feb | 48 | 15:30,18/Jul | 32 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY3WA | 18 | 21 | 16 | 13 | 16 | 17 | 23 | 18 | 190 | 190 |  |  |  | 1AGYMTMY7WA | 1A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 02:30,15/Feb | 47 | 10:30,24/Jul | 25 | 4C | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 4030998 | 12:00, January | 4030998 | 12:00, January | 4030998 | 4C | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 135045 | 04:30, May | 2015425 | 13:30, September | 727583
2B | TMY3 | 19 | 22 | 17 | 14 | 17 | 18 | 24 | 19 | 155 | 155 |  |  |  | 1AADMINTMY3WA | 1A | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 05:30,24/Jan | 57 | 21:30,18/Jul | 29 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | TMY2 | 18 | 21 | 16 | 13 | 16 | 17 | 23 | 18 | 188 | 188 |  |  |  | 1ALEARNING 1TMY3WA | 1A | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 06:30,02/Feb | 65 | 08:30,06/Jun | 33 | 5A | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 5085074 | 12:00, January | 5085074 | 12:00, January | 5085074 | 5A | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 130627 | 04:30, May | 2034786 | 13:30, September | 730709
2B | MIN | 16 | 18 | 14 | 11 | 14 | 15 | 18 | 16 | 222 | 222 |  |  |  | 1ALEARNING 2TMY3WA | 1A | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,31/Mar | 54 | 14:30,11/Sep | 23 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2B | MAX | 19 | 22 | 17 | 14 | 16 | 18 | 24 | 18 | 110 | 110 |  |  |  | 1APERFORMANCETMY3WA | 1A | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 09:30,23/Jan | 54 | 00:30,18/Jul | 23 | 5B | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 4896573 | 12:00, January | 4896573 | 12:00, January | 4896573 | 5B | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 104475 | 07:30, May | 1920098 | 13:30, September | 628307
3A | TMY15WA | 16 | 19 | 14 | 13 | 15 | 15 | 25 | 18 | 155 | 155 | 4399384 | 2052857 |  | 1ALEARNING 4TMY3WA | 1A | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 05:30,24/Jan | 53 | 10:30,05/Sep | 26 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY7WA | 16 | 18 | 14 | 12 | 14 | 15 | 24 | 17 | 164 | 164 |  |  |  | 1ALEARNING 3TMY3WA | 1A | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 07:30,02/Feb | 56 | 19:30,08/Sep | 28 | 5C | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 4138171 | 12:00, January | 4138171 | 12:00, January | 4138171 | 5C | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 55037 | 07:30, August | 1489545 | 13:30, September | 471065
3A | TMY3WA | 16 | 18 | 14 | 13 | 15 | 15 | 26 | 18 | 205 | 205 |  |  |  | 1AFOOD PREPTMY3WA | 1A | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 8 | 07:30,31/Mar | 48 | 15:30,21/Aug | 34 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY3 | 16 | 19 | 14 | 13 | 15 | 15 | 24 | 18 | 181 | 181 |  |  |  | 1AGYMTMY3WA | 1A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 05:30,24/Jan | 47 | 10:30,24/Jul | 28 | 6A | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 5360740 | 12:00, January | 5360740 | 12:00, January | 5360740 | 6A | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 135804 | 04:30, May | 1973973 | 13:30, September | 734807
3A | TMY2 | 15 | 18 | 14 | 12 | 14 | 15 | 24 | 17 | 189 | 189 |  |  |  | 1AADMINTMY3 | 1A | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,11/Jan | 56 | 08:30,01/Aug | 23 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | MIN | 16 | 18 | 15 | 13 | 15 | 15 | 19 | 16 | 251 | 251 |  |  |  | 1ALEARNING 1TMY3 | 1A | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,12/Nov | 63 | 09:30,01/Aug | 27 | 6B | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 5437763 | 12:00, January | 5437763 | 12:00, January | 5437763 | 6B | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 77939 | 07:30, September | 1819099 | 13:30, September | 608635
3A | MAX | 18 | 21 | 15 | 15 | 16 | 17 | 29 | 20 | 107 | 107 |  |  |  | 1ALEARNING 2TMY3 | 1A | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,15/Mar | 50 | 13:30,18/Sep | 19 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3B | TMY15WA | 16 | 18 | 14 | 11 | 14 | 15 | 19 | 16 | 149 | 149 | 3934210 | 2476394 |  | 1APERFORMANCETMY3 | 1A | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 09:30,09/Jan | 53 | 22:30,11/Jul | 20 | 7 | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 5448941 | 12:00, January | 5448941 | 12:00, January | 5448941 | 7 | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 80827 | 07:30, September | 1706564 | 13:30, September | 582425
3B | TMY7WA | 16 | 18 | 14 | 11 | 14 | 15 | 19 | 16 | 144 | 144 |  |  |  | 1ALEARNING 4TMY3 | 1A | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,25/Feb | 51 | 09:30,01/Aug | 21 |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3B | TMY3WA | 16 | 19 | 14 | 12 | 14 | 15 | 20 | 16 | 169 | 169 |  |  |  | 1ALEARNING 3TMY3 | 1A | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 07:30,12/Nov | 55 | 21:30,20/Sep | 23 | 8 | Heating plant sensible load | 80 rooms | RL.htg | Load (Btu/h) | 6235021 | 12:00, January | 6235021 | 12:00, January | 6235021 | 8 | Cooling plant sensible load | 80 rooms | RL.clg | Load (Btu/h) | 19368 | 07:30, September | 1524215 | 13:30, May | 512261
3B | TMY3 | 17 | 20 | 15 | 12 | 15 | 16 | 20 | 17 | 139 | 139 |  |  |  | 1AFOOD PREPTMY3 | 1A | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 6 | 08:30,16/Mar | 46 | 17:30,29/Jul | 31
3B | TMY2 | 16 | 19 | 15 | 12 | 14 | 15 | 20 | 16 | 159 | 159 |  |  |  | 1AGYMTMY3 | 1A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 17:30,10/Jan | 44 | 11:30,11/Sep | 25
3B | MIN | 15 | 17 | 14 | 11 | 14 | 14 | 16 | 15 | 199 | 199 |  |  |  | 1AADMINTMY2 | 1A | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 04:30,28/Dec | 56 | 00:30,28/Jun | 23
3B | MAX | 17 | 20 | 15 | 12 | 15 | 16 | 22 | 17 | 97 | 97 |  |  |  | 1ALEARNING 1TMY2 | 1A | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,23/Dec | 65 | 09:30,27/Jun | 26
3C | TMY7WA | 9 | 11 | 10 | 6 | 8 | 9 | 17 | 10 | 132 | 132 | 3542153 | 1819953 |  | 1ALEARNING 2TMY2 | 1A | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,07/Apr | 50 | 13:30,04/Jul | 18
3C | TMY3WA | 9 | 10 | 9 | 7 | 8 | 9 | 19 | 10 | 151 | 151 |  |  |  | 1APERFORMANCETMY2 | 1A | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 11:30,31/Jan | 54 | 01:30,28/Jun | 19
3C | TMY3 | 9 | 11 | 9 | 7 | 8 | 9 | 17 | 10 | 199 | 199 |  |  |  | 1ALEARNING 4TMY2 | 1A | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 06:30,07/Apr | 50 | 08:30,15/Aug | 21
3C | TMY2 | 10 | 11 | 10 | 7 | 8 | 9 | 16 | 10 | 142 | 142 |  |  |  | 1ALEARNING 3TMY2 | 1A | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 04:30,05/Jan | 54 | 19:30,07/Oct | 22
3C | TMY15WA | 9 | 11 | 9 | 7 | 8 | 9 | 17 | 10 | 152 | 152 |  |  |  | 1AFOOD PREPTMY2 | 1A | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 6 | 08:30,13/Jan | 47 | 12:30,04/Jul | 31
3C | MIN | 12 | 13 | 12 | 8 | 10 | 10 | 13 | 11 | 225 | 225 |  |  |  | 1AGYMTMY2 | 1A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 05:30,14/Jan | 44 | 10:30,14/Aug | 24
3C | MAX | 9 | 11 | 10 | 8 | 9 | 10 | 21 | 11 | 50 | 50 |  |  |  | 1AADMINMIN | 1A | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 00:30,26/Dec | 53 | 20:30,22/Aug | 18
4A | TMY15WA | 16 | 19 | 15 | 12 | 15 | 16 | 21 | 17 | 138 | 138 | 4495864 | 2141118 |  | 1ALEARNING 1MIN | 1A | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 06:30,29/Mar | 63 | 10:30,22/Aug | 21
4A | TMY3 | 16 | 18 | 14 | 12 | 15 | 16 | 20 | 16 | 149 | 149 |  |  |  | 1ALEARNING 2MIN | 1A | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 06:30,26/Mar | 49 | 16:30,22/Aug | 15
4A | TMY7WA | 16 | 18 | 14 | 12 | 14 | 16 | 21 | 16 | 180 | 180 |  |  |  | 1APERFORMANCEMIN | 1A | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 07:30,30/Dec | 53 | 23:30,22/Aug | 15
4A | TMY3WA | 16 | 19 | 15 | 12 | 15 | 16 | 22 | 17 | 165 | 165 |  |  |  | 1ALEARNING 4MIN | 1A | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 06:30,16/Feb | 48 | 13:30,15/Aug | 17
4A | TMY2 | 16 | 18 | 14 | 12 | 15 | 16 | 19 | 16 | 184 | 184 |  |  |  | 1ALEARNING 3MIN | 1A | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 07:30,09/Mar | 52 | 20:30,23/Aug | 18
4A | MIN | 16 | 17 | 14 | 12 | 14 | 15 | 16 | 15 | 248 | 248 |  |  |  | 1AFOOD PREPMIN | 1A | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 6 | 08:30,11/Jan | 45 | 17:30,30/Jul | 25
4A | MAX | 19 | 22 | 17 | 14 | 17 | 19 | 26 | 19 | 96 | 96 |  |  |  | 1AGYMMIN | 1A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 09:30,16/Dec | 44 | 10:30,24/Jul | 20
4B | TMY7WA | 14 | 16 | 13 | 10 | 13 | 14 | 17 | 15 | 171 | 171 | 4290498 | 1920707 |  | 1AADMINMAX | 1A | People dissatisfied | ADMIN | MAX | Percentage (%) | 7 | 06:30,15/Jan | 58 | 15:30,15/Aug | 32
4B | TMY3WA | 14 | 16 | 13 | 10 | 13 | 14 | 17 | 15 | 147 | 147 |  |  |  | 1ALEARNING 1MAX | 1A | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 6 | 06:30,15/Jan | 66 | 09:30,11/Jul | 36
4B | TMY3 | 15 | 17 | 13 | 11 | 14 | 14 | 17 | 15 | 207 | 207 |  |  |  | 1ALEARNING 2MAX | 1A | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 7 | 06:30,15/Jan | 56 | 15:30,15/Aug | 26
4B | TMY2 | 15 | 17 | 13 | 11 | 14 | 15 | 17 | 15 | 215 | 215 |  |  |  | 1APERFORMANCEMAX | 1A | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 13 | 09:30,18/Apr | 56 | 19:30,18/Jul | 25
4B | TMY15WA | 14 | 16 | 13 | 10 | 13 | 14 | 17 | 15 | 203 | 203 |  |  |  | 1ALEARNING 4MAX | 1A | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 7 | 07:30,15/Jan | 53 | 09:30,15/Aug | 28
4B | MIN | 16 | 18 | 15 | 12 | 15 | 15 | 15 | 15 | 243 | 243 |  |  |  | 1ALEARNING 3MAX | 1A | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 7 | 07:30,26/Jan | 56 | 21:30,06/Sep | 30
4B | MAX | 14 | 17 | 13 | 10 | 13 | 14 | 18 | 15 | 125 | 125 |  |  |  | 1AFOOD PREPMAX | 1A | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 15 | 07:30,12/Jan | 50 | 18:30,19/Aug | 35
4C | TMY7WA | 13 | 14 | 12 | 9 | 11 | 12 | 16 | 13 | 149 | 149 | 4030998 | 2015425 |  | 1AGYMMAX | 1A | People dissatisfied | GYM | MAX | Percentage (%) | 13 | 06:30,15/Jan | 46 | 10:30,14/Aug | 30
4C | TMY3WA | 12 | 13 | 11 | 8 | 10 | 11 | 16 | 12 | 150 | 150 |  |  |  | 2ALocationFilename | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
4C | TMY3 | 12 | 14 | 11 | 9 | 11 | 12 | 17 | 12 | 160 | 160 |  |  |  | 2AADMINTMY7WA | 2A | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 22:30,21/Feb | 56 | 23:30,15/Aug | 19
4C | TMY2 | 12 | 14 | 11 | 8 | 11 | 12 | 16 | 12 | 148 | 148 |  |  |  | 2ALEARNING 1TMY7WA | 2A | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,13/Jan | 64 | 10:30,12/Sep | 23
4C | TMY15WA | 12 | 14 | 11 | 8 | 11 | 12 | 16 | 12 | 153 | 153 |  |  |  | 2ALEARNING 2TMY7WA | 2A | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,18/Nov | 50 | 14:30,08/Aug | 16
4C | MIN | 15 | 16 | 14 | 10 | 13 | 14 | 12 | 14 | 221 | 221 |  |  |  | 2APERFORMANCETMY7WA | 2A | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 19:30,19/Jan | 49 | 03:30,16/Aug | 15
4C | MAX | 14 | 15 | 12 | 9 | 12 | 13 | 19 | 13 | 93 | 93 |  |  |  | 2ALEARNING 4TMY7WA | 2A | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,18/Nov | 48 | 13:30,07/Aug | 17
5A | TMY15WA | 16 | 18 | 14 | 12 | 14 | 16 | 19 | 16 | 123 | 123 | 5085074 | 2034786 |  | 2ALEARNING 3TMY7WA | 2A | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 08:30,21/Feb | 53 | 21:30,16/Aug | 18
5A | TMY7WA | 16 | 18 | 14 | 12 | 14 | 16 | 19 | 16 | 124 | 124 |  |  |  | 2AFOOD PREPTMY7WA | 2A | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 6 | 08:30,27/Dec | 46 | 11:30,13/Sep | 29
5A | TMY3WA | 15 | 17 | 14 | 11 | 14 | 15 | 20 | 16 | 139 | 139 |  |  |  | 2AGYMTMY7WA | 2A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 07:30,23/Feb | 44 | 11:30,03/Jul | 21
5A | TMY3 | 16 | 18 | 14 | 12 | 15 | 16 | 18 | 16 | 133 | 133 |  |  |  | 2AADMINTMY3WA | 2A | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,20/Jan | 56 | 23:30,15/Aug | 21
5A | TMY2 | 16 | 18 | 14 | 12 | 14 | 15 | 18 | 16 | 144 | 144 |  |  |  | 2ALEARNING 1TMY3WA | 2A | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,16/Apr | 63 | 08:30,19/Jun | 24
5A | MIN | 16 | 18 | 15 | 12 | 15 | 16 | 15 | 15 | 177 | 177 |  |  |  | 2ALEARNING 2TMY3WA | 2A | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,08/Dec | 50 | 13:30,18/Sep | 17
5A | MAX | 17 | 19 | 15 | 12 | 15 | 17 | 23 | 17 | 78 | 78 |  |  |  | 2APERFORMANCETMY3WA | 2A | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 08:30,23/Jan | 49 | 03:30,16/Aug | 16
5B | TMY7WA | 15 | 16 | 14 | 11 | 13 | 14 | 14 | 14 | 148 | 148 | 4896573 | 1920098 |  | 2ALEARNING 4TMY3WA | 2A | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 06:30,20/Jan | 48 | 12:30,01/Aug | 19
5B | TMY3WA | 14 | 16 | 14 | 10 | 13 | 14 | 14 | 14 | 166 | 166 |  |  |  | 2ALEARNING 3TMY3WA | 2A | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 10:30,21/Feb | 53 | 21:30,16/Aug | 20
5B | TMY3 | 14 | 16 | 13 | 10 | 13 | 14 | 16 | 14 | 146 | 146 |  |  |  | 2AFOOD PREPTMY3WA | 2A | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 6 | 08:30,20/Dec | 48 | 12:30,28/Sep | 30
5B | TMY2 | 14 | 16 | 13 | 10 | 13 | 14 | 16 | 14 | 158 | 158 |  |  |  | 2AGYMTMY3WA | 2A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 07:30,01/Feb | 44 | 10:30,07/Aug | 22
5B | TMY15WA | 14 | 16 | 13 | 10 | 13 | 14 | 14 | 14 | 165 | 165 |  |  |  | 2AADMINTMY3 | 2A | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 05:30,01/Feb | 56 | 13:30,29/Aug | 18
5B | MIN | 19 | 20 | 17 | 14 | 17 | 18 | 14 | 17 | 186 | 186 |  |  |  | 2ALEARNING 1TMY3 | 2A | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,16/Dec | 63 | 10:30,29/Aug | 22
5B | MAX | 13 | 15 | 12 | 9 | 12 | 13 | 16 | 14 | 84 | 84 |  |  |  | 2ALEARNING 2TMY3 | 2A | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,29/Nov | 50 | 13:30,29/Aug | 15
5C | TMY7WA | 12 | 13 | 11 | 8 | 10 | 12 | 15 | 12 | 156 | 156 | 4138171 | 1489545 |  | 2APERFORMANCETMY3 | 2A | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 17:30,13/Jan | 47 | 21:30,11/Jul | 15
5C | TMY3WA | 11 | 13 | 11 | 8 | 10 | 11 | 16 | 11 | 177 | 177 |  |  |  | 2ALEARNING 4TMY3 | 2A | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 06:30,22/Mar | 47 | 11:30,29/Aug | 17
5C | TMY15WA | 12 | 13 | 11 | 8 | 10 | 11 | 15 | 11 | 144 | 144 |  |  |  | 2ALEARNING 3TMY3 | 2A | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 10:30,04/Jan | 50 | 21:30,03/Aug | 18
5C | MAX | 11 | 13 | 11 | 8 | 10 | 12 | 18 | 12 | 507 | 507 |  |  |  | 2AFOOD PREPTMY3 | 2A | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,11/Feb | 45 | 14:30,20/Jun | 28
5C | MIN | 15 | 16 | 13 | 10 | 13 | 14 | 13 | 14 | 99 | 99 |  |  |  | 2AGYMTMY3 | 2A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 14:30,20/Dec | 43 | 10:30,31/Jul | 20
5C | doeCWEC | 12 | 14 | 11 | 8 | 11 | 12 | 15 | 12 | 0 | 0 |  |  |  | 2AADMINTMY2 | 2A | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 07:30,21/Feb | 53 | 09:30,18/Jul | 18
5C | CWEC | 12 | 13 | 11 | 8 | 11 | 12 | 15 | 12 | 228 | 228 |  |  |  | 2ALEARNING 1TMY2 | 2A | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,25/Jan | 64 | 10:30,18/Jul | 21
5C | TMY7WA | 12 | 13 | 11 | 8 | 10 | 12 | 15 | 12 | 136 | 136 | 5360740 | 1973973 |  | 2ALEARNING 2TMY2 | 2A | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,29/Nov | 46 | 15:30,31/Jul | 15
6A | TMY3WA | 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 124 | 124 |  |  |  | 2APERFORMANCETMY2 | 2A | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 20:30,07/Dec | 46 | 21:30,18/Jul | 14
6A | TMY3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 152 | 152 |  |  |  | 2ALEARNING 4TMY2 | 2A | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 06:30,01/Dec | 46 | 10:30,18/Jul | 16
6A | TMY2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 125 | 125 |  |  |  | 2ALEARNING 3TMY2 | 2A | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 13:30,07/Mar | 49 | 21:30,30/Aug | 17
6A | TMY15WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142 | 142 |  |  |  | 2AFOOD PREPTMY2 | 2A | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,10/Dec | 44 | 13:30,18/Jul | 28
6A | MIN | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 169 | 169 |  |  |  | 2AGYMTMY2 | 2A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 07:30,05/Mar | 43 | 11:30,31/Jul | 20
6A | MAX | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88 | 88 |  |  |  | 2AADMINTMY15WA | 2A | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 05:30,03/Feb | 56 | 23:30,15/Aug | 19
6A | TMY7WA | 16 | 18 | 15 | 12 | 15 | 16 | 18 | 16 | 117 | 117 | 5437763 | 1819099 |  | 2ALEARNING 1TMY15WA | 2A | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,28/Jan | 64 | 10:30,12/Sep | 23
6B | TMY3WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 127 | 127 |  |  |  | 2ALEARNING 2TMY15WA | 2A | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 08:30,12/Jan | 50 | 14:30,08/Aug | 17
6B | TMY3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 129 | 129 |  |  |  | 2APERFORMANCETMY15WA | 2A | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 13:30,10/Jan | 49 | 03:30,16/Aug | 16
6B | TMY2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1712 | 1712 |  |  |  | 2ALEARNING 4TMY15WA | 2A | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 06:30,19/Jan | 48 | 14:30,22/Aug | 18
6B | TMY15WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 116 | 116 |  |  |  | 2ALEARNING 3TMY15WA | 2A | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 08:30,21/Feb | 55 | 21:30,16/Aug | 20
6B | MIN | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 149 | 149 |  |  |  | 2AFOOD PREPTMY15WA | 2A | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 6 | 07:30,27/Dec | 46 | 14:30,12/Sep | 29
6B | MAX | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 70 | 70 |  |  |  | 2AGYMTMY15WA | 2A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 15:30,12/Jan | 44 | 10:30,07/Aug | 21
6B | TMY7WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 114 | 114 | 5448941 | 1706564 |  | 2AADMINMIN | 2A | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 05:30,22/Apr | 49 | 13:30,07/Aug | 17
7 | TMY3WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 118 | 118 |  |  |  | 2ALEARNING 1MIN | 2A | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,30/Sep | 61 | 16:30,25/Jul | 20
7 | TMY3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 143 | 143 |  |  |  | 2ALEARNING 2MIN | 2A | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,29/Apr | 44 | 14:30,07/Aug | 15
7 | TMY2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 128 | 128 |  |  |  | 2APERFORMANCEMIN | 2A | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 20:30,18/Oct | 42 | 20:30,13/Jun | 13
7 | TMY15WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 140 | 140 |  |  |  | 2ALEARNING 4MIN | 2A | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 06:30,21/Apr | 45 | 14:30,07/Aug | 16
7 | MIN | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 184 | 184 |  |  |  | 2ALEARNING 3MIN | 2A | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 06:30,11/Oct | 46 | 15:30,08/Aug | 16
7 | MAX | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 78 | 78 |  |  |  | 2AFOOD PREPMIN | 2A | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,04/Feb | 44 | 17:30,30/Jul | 22
7 | Filename | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 91 | 91 | 6235021 | 1524215 |  | 2AGYMMIN | 2A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 14:30,03/Mar | 43 | 10:30,31/Jul | 18
8 | TMY15WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 95 | 95 |  |  |  | 2AADMINMAX | 2A | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 05:30,18/Jan | 56 | 01:30,16/Aug | 24
8 | TMY7WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 104 | 104 |  |  |  | 2ALEARNING 1MAX | 2A | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 6 | 06:30,25/Jan | 63 | 10:30,15/Aug | 28
8 | TMY3WA | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 92 | 92 |  |  |  | 2ALEARNING 2MAX | 2A | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 6 | 05:30,08/Feb | 52 | 13:30,08/Aug | 20
8 | TMY3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 102 | 102 |  |  |  | 2APERFORMANCEMAX | 2A | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 20:30,28/Dec | 51 | 04:30,16/Aug | 20
8 | TMY2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 120 | 120 |  |  |  | 2ALEARNING 4MAX | 2A | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 6 | 05:30,18/Jan | 50 | 12:30,08/Aug | 22
8 | MIN | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 65 | 65 |  |  |  | 2ALEARNING 3MAX | 2A | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 6 | 05:30,27/Dec | 52 | 12:30,04/Sep | 23
8 | MAX | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | 2AFOOD PREPMAX | 2A | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 12 | 07:30,13/Dec | 51 | 12:30,31/May | 33
[15 empty] | 2AGYMMAX | 2A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 04:30,18/Jan | 44 | 11:30,03/Jul | 25
[15 empty] | 2BLocationFilename | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 2BADMINTMY15WA | 2B | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,16/Apr | 54 | 13:30,25/Jul | 17
[15 empty] | 2BLEARNING 1TMY15WA | 2B | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 06:30,28/Apr | 59 | 14:30,15/Aug | 20
[15 empty] | 2BLEARNING 2TMY15WA | 2B | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,25/Feb | 51 | 14:30,25/Jul | 15
[15 empty] | 2BPERFORMANCETMY15WA | 2B | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 12:30,25/Dec | 51 | 04:30,26/Jul | 13
[15 empty] | 2BLEARNING 4TMY15WA | 2B | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,23/Feb | 48 | 15:30,15/Aug | 15
[15 empty] | 2BLEARNING 3TMY15WA | 2B | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 07:30,15/Apr | 49 | 13:30,14/Aug | 17
[15 empty] | 2BFOOD PREPTMY15WA | 2B | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 06:30,20/Dec | 45 | 17:30,26/Jul | 22
[15 empty] | 2BGYMTMY15WA | 2B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,15/Feb | 43 | 10:30,24/Jul | 17
[15 empty] | 2BADMINTMY7WA | 2B | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 06:30,26/Mar | 54 | 14:30,29/Aug | 16
[15 empty] | 2BLEARNING 1TMY7WA | 2B | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,26/Nov | 60 | 12:30,22/Aug | 19
[15 empty] | 2BLEARNING 2TMY7WA | 2B | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,19/Nov | 50 | 14:30,28/Aug | 15
[15 empty] | 2BPERFORMANCETMY7WA | 2B | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 10:30,28/Nov | 49 | 22:30,01/Aug | 12
[15 empty] | 2BLEARNING 4TMY7WA | 2B | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,23/Feb | 47 | 11:30,10/Jul | 14
[15 empty] | 2BLEARNING 3TMY7WA | 2B | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,30/Mar | 50 | 11:30,10/Jul | 16
[15 empty] | 2BFOOD PREPTMY7WA | 2B | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 06:30,30/Dec | 45 | 13:30,21/Aug | 22
[15 empty] | 2BGYMTMY7WA | 2B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 09:30,15/Feb | 43 | 10:30,14/Aug | 17
[15 empty] | 2BADMINTMY3WA | 2B | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,25/Nov | 54 | 13:30,25/Jul | 18
[15 empty] | 2BLEARNING 1TMY3WA | 2B | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,25/Nov | 59 | 12:30,17/Jul | 21
[15 empty] | 2BLEARNING 2TMY3WA | 2B | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,24/Nov | 51 | 15:30,25/Jul | 16
[15 empty] | 2BPERFORMANCETMY3WA | 2B | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 16:30,20/Dec | 51 | 03:30,26/Jul | 13
[15 empty] | 2BLEARNING 4TMY3WA | 2B | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,26/Nov | 48 | 11:30,17/Jul | 16
[15 empty] | 2BLEARNING 3TMY3WA | 2B | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 07:30,25/Nov | 49 | 21:30,16/Aug | 17
[15 empty] | 2BFOOD PREPTMY3WA | 2B | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 06:30,03/Dec | 46 | 13:30,15/Aug | 23
[15 empty] | 2BGYMTMY3WA | 2B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 07:30,16/Feb | 43 | 11:30,24/Jul | 18
[15 empty] | 2BADMINTMY3 | 2B | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,16/Feb | 54 | 14:30,07/Aug | 19
[15 empty] | 2BLEARNING 1TMY3 | 2B | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,18/Mar | 60 | 13:30,24/Jul | 22
[15 empty] | 2BLEARNING 2TMY3 | 2B | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,03/Mar | 52 | 15:30,25/Jul | 17
[15 empty] | 2BPERFORMANCETMY3 | 2B | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 07:30,05/Apr | 53 | 23:30,08/Aug | 14
[15 empty] | 2BLEARNING 4TMY3 | 2B | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 06:30,02/Apr | 49 | 13:30,08/Aug | 17
[15 empty] | 2BLEARNING 3TMY3 | 2B | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 07:30,21/Apr | 51 | 12:30,07/Aug | 18
[15 empty] | 2BFOOD PREPTMY3 | 2B | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 07:30,20/Dec | 47 | 13:30,24/Jul | 24
[15 empty] | 2BGYMTMY3 | 2B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,26/Jan | 44 | 10:30,10/Jul | 19
[15 empty] | 2BADMINTMY2 | 2B | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 06:30,29/Jan | 53 | 13:30,11/Jul | 18
[15 empty] | 2BLEARNING 1TMY2 | 2B | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 06:30,02/Mar | 59 | 12:30,11/Sep | 21
[15 empty] | 2BLEARNING 2TMY2 | 2B | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,15/Nov | 50 | 15:30,11/Jul | 16
[15 empty] | 2BPERFORMANCETMY2 | 2B | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 10:30,02/Feb | 51 | 04:30,12/Jul | 13
[15 empty] | 2BLEARNING 4TMY2 | 2B | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 06:30,02/Mar | 48 | 11:30,17/Jul | 16
[15 empty] | 2BLEARNING 3TMY2 | 2B | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 07:30,27/Jan | 49 | 12:30,17/Jul | 17
[15 empty] | 2BFOOD PREPTMY2 | 2B | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,27/Dec | 46 | 13:30,11/Jul | 23
[15 empty] | 2BGYMTMY2 | 2B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 09:30,16/Feb | 43 | 10:30,17/Jul | 18
[15 empty] | 2BADMINMIN | 2B | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 06:30,25/Oct | 47 | 15:30,11/Jul | 16
[15 empty] | 2BLEARNING 1MIN | 2B | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 06:30,14/Jun | 57 | 14:30,11/Jul | 18
[15 empty] | 2BLEARNING 2MIN | 2B | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,06/Oct | 43 | 16:30,11/Jul | 14
[15 empty] | 2BPERFORMANCEMIN | 2B | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 13:30,08/Mar | 44 | 20:30,11/Jul | 11
[15 empty] | 2BLEARNING 4MIN | 2B | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 06:30,28/May | 41 | 15:30,11/Jul | 14
[15 empty] | 2BLEARNING 3MIN | 2B | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 06:30,08/Jun | 47 | 21:30,20/Jul | 15
[15 empty] | 2BFOOD PREPMIN | 2B | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 06:30,25/Jan | 43 | 17:30,27/Jul | 18
[15 empty] | 2BGYMMIN | 2B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 09:30,25/Feb | 41 | 17:30,08/Sep | 16
[15 empty] | 2BADMINMAX | 2B | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,23/Feb | 54 | 11:30,04/Sep | 19
[15 empty] | 2BLEARNING 1MAX | 2B | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,19/Mar | 62 | 12:30,04/Sep | 22
[15 empty] | 2BLEARNING 2MAX | 2B | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,21/Jan | 52 | 16:30,25/Jul | 17
[15 empty] | 2BPERFORMANCEMAX | 2B | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 07:30,04/Jan | 52 | 00:30,26/Jul | 14
[15 empty] | 2BLEARNING 4MAX | 2B | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,03/Mar | 47 | 15:30,25/Jul | 16
[15 empty] | 2BLEARNING 3MAX | 2B | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 07:30,21/Jan | 52 | 15:30,11/Jul | 18
[15 empty] | 2BFOOD PREPMAX | 2B | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 07:30,06/Dec | 46 | 14:30,25/Jul | 24
[15 empty] | 2BGYMMAX | 2B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 08:30,01/Dec | 43 | 10:30,04/Sep | 18
[15 empty] | 3ALocationFilename | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 3AADMINTMY15WA | 3A | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,22/Mar | 52 | 15:30,01/Aug | 16
[15 empty] | 3ALEARNING 1TMY15WA | 3A | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,10/Mar | 62 | 10:30,25/Jul | 19
[15 empty] | 3ALEARNING 2TMY15WA | 3A | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,21/Oct | 47 | 15:30,25/Jul | 14
[15 empty] | 3APERFORMANCETMY15WA | 3A | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 09:30,09/Mar | 46 | 20:30,25/Jul | 13
[15 empty] | 3ALEARNING 4TMY15WA | 3A | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,03/May | 48 | 14:30,01/Aug | 15
[15 empty] | 3ALEARNING 3TMY15WA | 3A | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 12:30,29/Nov | 49 | 14:30,01/Aug | 15
[15 empty] | 3AFOOD PREPTMY15WA | 3A | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,02/Feb | 44 | 17:30,21/Aug | 25
[15 empty] | 3AGYMTMY15WA | 3A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 09:30,19/Jan | 43 | 11:30,24/Jul | 18
[15 empty] | 3AADMINTMY7WA | 3A | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 05:30,08/Apr | 53 | 15:30,01/Aug | 16
[15 empty] | 3ALEARNING 1TMY7WA | 3A | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,27/Jan | 62 | 10:30,25/Jul | 18
[15 empty] | 3ALEARNING 2TMY7WA | 3A | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 08:30,12/Nov | 47 | 13:30,01/Aug | 14
[15 empty] | 3APERFORMANCETMY7WA | 3A | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 09:30,05/Nov | 45 | 21:30,25/Jul | 12
[15 empty] | 3ALEARNING 4TMY7WA | 3A | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,06/Oct | 48 | 14:30,01/Aug | 14
[15 empty] | 3ALEARNING 3TMY7WA | 3A | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 11:30,18/Jan | 49 | 14:30,01/Aug | 15
[15 empty] | 3AFOOD PREPTMY7WA | 3A | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,13/Jan | 44 | 12:30,24/Jul | 24
[15 empty] | 3AGYMTMY7WA | 3A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 08:30,06/Jan | 43 | 11:30,24/Jul | 17
[15 empty] | 3AADMINTMY3WA | 3A | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,12/Apr | 51 | 14:30,25/Jul | 16
[15 empty] | 3ALEARNING 1TMY3WA | 3A | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,15/Dec | 61 | 14:30,25/Jul | 18
[15 empty] | 3ALEARNING 2TMY3WA | 3A | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,06/Apr | 46 | 15:30,25/Jul | 14
[15 empty] | 3APERFORMANCETMY3WA | 3A | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 16:30,31/Dec | 44 | 20:30,27/Jun | 13
[15 empty] | 3ALEARNING 4TMY3WA | 3A | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,06/Apr | 45 | 14:30,25/Jul | 15
[15 empty] | 3ALEARNING 3TMY3WA | 3A | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 06:30,06/Dec | 48 | 15:30,25/Jul | 15
[15 empty] | 3AFOOD PREPTMY3WA | 3A | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 6 | 08:30,25/Feb | 45 | 11:30,24/Jul | 26
[15 empty] | 3AGYMTMY3WA | 3A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 09:30,19/Jan | 42 | 11:30,29/May | 18
[15 empty] | 3AADMINTMY3 | 3A | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,28/Oct | 47 | 14:30,01/Aug | 16
[15 empty] | 3ALEARNING 1TMY3 | 3A | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 06:30,09/Jun | 58 | 13:30,01/Aug | 19
[15 empty] | 3ALEARNING 2TMY3 | 3A | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,11/Mar | 41 | 16:30,17/Jul | 14
[15 empty] | 3APERFORMANCETMY3 | 3A | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 19:30,24/Dec | 40 | 21:30,15/Aug | 13
[15 empty] | 3ALEARNING 4TMY3 | 3A | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,11/Mar | 43 | 14:30,01/Aug | 15
[15 empty] | 3ALEARNING 3TMY3 | 3A | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 10:30,27/Dec | 44 | 20:30,19/Aug | 15
[15 empty] | 3AFOOD PREPTMY3 | 3A | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,08/Jan | 44 | 17:30,14/Aug | 24
[15 empty] | 3AGYMTMY3 | 3A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 15:30,13/Jan | 42 | 17:30,09/Sep | 18
[15 empty] | 3AADMINTMY2 | 3A | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 01:30,18/Oct | 50 | 13:30,04/Jul | 15
[15 empty] | 3ALEARNING 1TMY2 | 3A | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,07/Jan | 59 | 12:30,04/Jul | 18
[15 empty] | 3ALEARNING 2TMY2 | 3A | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,18/Mar | 43 | 14:30,03/Jul | 14
[15 empty] | 3APERFORMANCETMY2 | 3A | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 07:30,07/Jan | 41 | 05:30,15/Jan | 12
[15 empty] | 3ALEARNING 4TMY2 | 3A | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 06:30,10/Nov | 43 | 15:30,03/Jul | 14
[15 empty] | 3ALEARNING 3TMY2 | 3A | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 10:30,17/Oct | 45 | 13:30,03/Jul | 15
[15 empty] | 3AFOOD PREPTMY2 | 3A | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,13/Jan | 45 | 19:30,03/Jul | 24
[15 empty] | 3AGYMTMY2 | 3A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,29/Dec | 42 | 10:30,03/Jul | 17
[15 empty] | 3AADMINMIN | 3A | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 16:30,30/May | 42 | 08:30,24/Jan | 16
[15 empty] | 3ALEARNING 1MIN | 3A | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,15/Apr | 49 | 17:30,29/Aug | 18
[15 empty] | 3ALEARNING 2MIN | 3A | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,24/Sep | 39 | 22:30,23/Jan | 15
[15 empty] | 3APERFORMANCEMIN | 3A | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 07:30,06/Oct | 43 | 05:30,08/Jan | 13
[15 empty] | 3ALEARNING 4MIN | 3A | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 06:30,04/May | 38 | 02:30,24/Jan | 15
[15 empty] | 3ALEARNING 3MIN | 3A | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 06:30,08/Jun | 39 | 19:30,09/Aug | 15
[15 empty] | 3AFOOD PREPMIN | 3A | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,02/Feb | 41 | 17:30,01/Aug | 19
[15 empty] | 3AGYMMIN | 3A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 07:30,28/Apr | 41 | 02:30,25/Jan | 16
[15 empty] | 3AADMINMAX | 3A | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 10:30,05/Dec | 53 | 13:30,22/Aug | 18
[15 empty] | 3ALEARNING 1MAX | 3A | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 07:30,18/Feb | 62 | 11:30,25/Jul | 21
[15 empty] | 3ALEARNING 2MAX | 3A | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,26/Nov | 48 | 15:30,22/Aug | 15
[15 empty] | 3APERFORMANCEMAX | 3A | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 08:30,25/Dec | 48 | 19:30,08/Aug | 15
[15 empty] | 3ALEARNING 4MAX | 3A | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 06:30,09/Feb | 47 | 14:30,18/Jul | 16
[15 empty] | 3ALEARNING 3MAX | 3A | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 15:30,21/Feb | 49 | 14:30,18/Jul | 17
[15 empty] | 3AFOOD PREPMAX | 3A | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 7 | 07:30,08/Feb | 45 | 12:30,24/Jul | 29
[15 empty] | 3AGYMMAX | 3A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 15:30,03/Jan | 42 | 12:30,24/Jul | 20
[15 empty] | 3BLocationFilename | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 3BADMINTMY15WA | 3B | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 07:30,05/Apr | 48 | 14:30,01/Aug | 16
[15 empty] | 3BLEARNING 1TMY15WA | 3B | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,22/Oct | 53 | 12:30,04/Sep | 18
[15 empty] | 3BLEARNING 2TMY15WA | 3B | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,16/Mar | 44 | 17:30,25/Jul | 14
[15 empty] | 3BPERFORMANCETMY15WA | 3B | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 12:30,23/Jan | 50 | 21:30,25/Jul | 11
[15 empty] | 3BLEARNING 4TMY15WA | 3B | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,31/Mar | 42 | 11:30,31/Jul | 14
[15 empty] | 3BLEARNING 3TMY15WA | 3B | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 07:30,22/Mar | 46 | 21:30,02/Aug | 15
[15 empty] | 3BFOOD PREPTMY15WA | 3B | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,06/Jan | 42 | 11:30,06/Sep | 19
[15 empty] | 3BGYMTMY15WA | 3B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 15:30,15/Feb | 41 | 10:30,31/Jul | 16
[15 empty] | 3BADMINTMY7WA | 3B | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 06:30,16/Mar | 47 | 14:30,25/Jul | 16
[15 empty] | 3BLEARNING 1TMY7WA | 3B | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 06:30,05/May | 55 | 11:30,18/Sep | 18
[15 empty] | 3BLEARNING 2TMY7WA | 3B | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,15/Mar | 44 | 17:30,25/Jul | 14
[15 empty] | 3BPERFORMANCETMY7WA | 3B | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 12:30,23/Jan | 50 | 21:30,25/Jul | 11
[15 empty] | 3BLEARNING 4TMY7WA | 3B | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,05/Apr | 42 | 11:30,31/Jul | 14
[15 empty] | 3BLEARNING 3TMY7WA | 3B | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,03/May | 47 | 19:30,07/Sep | 15
[15 empty] | 3BFOOD PREPTMY7WA | 3B | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,06/Jan | 43 | 11:30,07/Sep | 19
[15 empty] | 3BGYMTMY7WA | 3B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 15:30,10/Dec | 41 | 10:30,31/Jul | 16
[15 empty] | 3BADMINTMY3WA | 3B | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,15/Apr | 50 | 13:30,07/Aug | 16
[15 empty] | 3BLEARNING 1TMY3WA | 3B | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,14/Oct | 57 | 13:30,07/Aug | 19
[15 empty] | 3BLEARNING 2TMY3WA | 3B | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,23/Apr | 46 | 14:30,21/Aug | 14
[15 empty] | 3BPERFORMANCETMY3WA | 3B | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 13:30,28/Jan | 50 | 21:30,25/Jul | 12
[15 empty] | 3BLEARNING 4TMY3WA | 3B | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,31/Mar | 46 | 12:30,07/Aug | 14
[15 empty] | 3BLEARNING 3TMY3WA | 3B | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 07:30,22/Mar | 47 | 12:30,08/Aug | 15
[15 empty] | 3BFOOD PREPTMY3WA | 3B | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 08:30,22/Dec | 43 | 15:30,21/Aug | 20
[15 empty] | 3BGYMTMY3WA | 3B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 07:30,02/Feb | 42 | 11:30,07/Aug | 16
[15 empty] | 3BADMINTMY3 | 3B | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,16/Apr | 52 | 12:30,07/Aug | 17
[15 empty] | 3BLEARNING 1TMY3 | 3B | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 06:30,26/Apr | 58 | 13:30,07/Aug | 20
[15 empty] | 3BLEARNING 2TMY3 | 3B | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,02/Apr | 48 | 12:30,07/Aug | 15
[15 empty] | 3BPERFORMANCETMY3 | 3B | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 09:30,17/Mar | 49 | 22:30,08/Aug | 12
[15 empty] | 3BLEARNING 4TMY3 | 3B | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,05/Nov | 45 | 12:30,07/Aug | 15
[15 empty] | 3BLEARNING 3TMY3 | 3B | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 07:30,01/Nov | 47 | 20:30,21/Jun | 16
[15 empty] | 3BFOOD PREPTMY3 | 3B | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 07:30,08/Mar | 44 | 11:30,02/Sep | 20
[15 empty] | 3BGYMTMY3 | 3B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,22/Dec | 43 | 10:30,07/Aug | 17
[15 empty] | 3BADMINTMY2 | 3B | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 06:30,16/Apr | 52 | 12:30,07/Aug | 16
[15 empty] | 3BLEARNING 1TMY2 | 3B | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 06:30,26/Apr | 57 | 12:30,07/Aug | 19
[15 empty] | 3BLEARNING 2TMY2 | 3B | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,14/Oct | 47 | 12:30,07/Aug | 15
[15 empty] | 3BPERFORMANCETMY2 | 3B | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 07:30,17/Nov | 48 | 22:30,07/Aug | 12
[15 empty] | 3BLEARNING 4TMY2 | 3B | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,19/Apr | 45 | 11:30,10/Jul | 14
[15 empty] | 3BLEARNING 3TMY2 | 3B | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 07:30,28/Apr | 47 | 12:30,07/Aug | 15
[15 empty] | 3BFOOD PREPTMY2 | 3B | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 07:30,27/Dec | 43 | 17:30,05/Aug | 20
[15 empty] | 3BGYMTMY2 | 3B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,05/Feb | 43 | 10:30,07/Aug | 16
[15 empty] | 3BADMINMIN | 3B | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,10/Jun | 43 | 15:30,31/Jul | 15
[15 empty] | 3BLEARNING 1MIN | 3B | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,03/Jun | 53 | 16:30,31/Jul | 17
[15 empty] | 3BLEARNING 2MIN | 3B | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,14/May | 37 | 15:30,22/Aug | 14
[15 empty] | 3BPERFORMANCEMIN | 3B | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 07:30,20/Oct | 41 | 05:30,18/Jan | 11
[15 empty] | 3BLEARNING 4MIN | 3B | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,08/Jun | 39 | 15:30,31/Jul | 14
[15 empty] | 3BLEARNING 3MIN | 3B | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 07:30,01/Jun | 42 | 13:30,31/Jul | 14
[15 empty] | 3BFOOD PREPMIN | 3B | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,23/Feb | 41 | 11:30,13/Aug | 16
[15 empty] | 3BGYMMIN | 3B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 08:30,31/Mar | 40 | 14:30,31/Jul | 15
[15 empty] | 3BADMINMAX | 3B | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,15/Mar | 51 | 13:30,05/Sep | 17
[15 empty] | 3BLEARNING 1MAX | 3B | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,08/Apr | 57 | 17:30,01/Sep | 20
[15 empty] | 3BLEARNING 2MAX | 3B | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,12/Nov | 47 | 12:30,24/Jul | 15
[15 empty] | 3BPERFORMANCEMAX | 3B | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 19:30,22/Jan | 44 | 20:30,04/Jul | 12
[15 empty] | 3BLEARNING 4MAX | 3B | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,28/Oct | 45 | 11:30,24/Jul | 15
[15 empty] | 3BLEARNING 3MAX | 3B | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 07:30,28/Oct | 48 | 12:30,05/Sep | 16
[15 empty] | 3BFOOD PREPMAX | 3B | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 07:30,27/Dec | 44 | 11:30,06/Sep | 22
[15 empty] | 3BGYMMAX | 3B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 09:30,29/Dec | 42 | 11:30,03/Jul | 17
[15 empty] | 3CLocationFilename | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 3CADMINTMY7WA | 3C | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 06:30,16/Nov | 28 | 04:30,11/Jan | 9
[15 empty] | 3CLEARNING 1TMY7WA | 3C | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,15/Jun | 32 | 06:30,10/Jan | 11
[15 empty] | 3CLEARNING 2TMY7WA | 3C | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,29/Jan | 28 | 03:30,11/Jan | 10
[15 empty] | 3CPERFORMANCETMY7WA | 3C | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 18:30,19/Feb | 24 | 05:30,11/Jan | 6
[15 empty] | 3CLEARNING 4TMY7WA | 3C | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,29/Oct | 26 | 03:30,11/Jan | 8
[15 empty] | 3CLEARNING 3TMY7WA | 3C | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 10:30,31/Oct | 25 | 03:30,11/Jan | 9
[15 empty] | 3CFOOD PREPTMY7WA | 3C | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,11/Jan | 38 | 13:30,14/Oct | 17
[15 empty] | 3CGYMTMY7WA | 3C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 06:30,21/Jun | 33 | 04:30,11/Jan | 10
[15 empty] | 3CADMINTMY3WA | 3C | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 08:30,18/Jul | 33 | 14:30,02/Oct | 9
[15 empty] | 3CLEARNING 1TMY3WA | 3C | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,15/Apr | 38 | 15:30,02/Oct | 10
[15 empty] | 3CLEARNING 2TMY3WA | 3C | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,12/Mar | 25 | 04:30,08/Feb | 9
[15 empty] | 3CPERFORMANCETMY3WA | 3C | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 09:30,27/Nov | 22 | 05:30,08/Feb | 7
[15 empty] | 3CLEARNING 4TMY3WA | 3C | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,12/Mar | 27 | 13:30,04/Sep | 8
[15 empty] | 3CLEARNING 3TMY3WA | 3C | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 08:30,18/Jul | 32 | 13:30,25/Sep | 9
[15 empty] | 3CFOOD PREPTMY3WA | 3C | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 08:30,09/Feb | 39 | 11:30,04/Oct | 19
[15 empty] | 3CGYMTMY3WA | 3C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 07:30,23/Mar | 35 | 11:30,04/Sep | 10
[15 empty] | 3CADMINTMY3 | 3C | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,30/Aug | 27 | 04:30,11/Jan | 9
[15 empty] | 3CLEARNING 1TMY3 | 3C | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,18/Jun | 34 | 18:30,02/Apr | 11
[15 empty] | 3CLEARNING 2TMY3 | 3C | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 08:30,22/Dec | 27 | 04:30,27/Dec | 9
[15 empty] | 3CPERFORMANCETMY3 | 3C | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 19:30,01/Dec | 23 | 05:30,27/Dec | 7
[15 empty] | 3CLEARNING 4TMY3 | 3C | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 06:30,18/Jun | 25 | 04:30,27/Dec | 8
[15 empty] | 3CLEARNING 3TMY3 | 3C | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 11:30,11/Jul | 26 | 14:30,04/Sep | 9
[15 empty] | 3CFOOD PREPTMY3 | 3C | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 07:30,25/Jan | 38 | 13:30,23/Sep | 17
[15 empty] | 3CGYMTMY3 | 3C | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 10:30,11/Jul | 37 | 17:30,02/Apr | 10
[15 empty] | 3CADMINTMY2 | 3C | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 11:30,22/Aug | 30 | 06:30,26/Dec | 10
[15 empty] | 3CLEARNING 1TMY2 | 3C | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,08/Jun | 41 | 15:30,03/Jul | 11
[15 empty] | 3CLEARNING 2TMY2 | 3C | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 08:30,31/Dec | 29 | 05:30,26/Dec | 10
[15 empty] | 3CPERFORMANCETMY2 | 3C | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 17:30,23/Nov | 24 | 05:30,26/Dec | 7
[15 empty] | 3CLEARNING 4TMY2 | 3C | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 06:30,29/Jun | 28 | 14:30,03/Jul | 8
[15 empty] | 3CLEARNING 3TMY2 | 3C | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 10:30,17/Oct | 29 | 18:30,28/Sep | 9
[15 empty] | 3CFOOD PREPTMY2 | 3C | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,22/Dec | 39 | 12:30,29/Sep | 16
[15 empty] | 3CGYMTMY2 | 3C | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 05:30,16/Jul | 37 | 17:30,28/Sep | 10
[15 empty] | 3CADMINTMY15WA | 3C | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,16/Nov | 34 | 12:30,18/Sep | 9
[15 empty] | 3CLEARNING 1TMY15WA | 3C | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,10/May | 44 | 13:30,18/Sep | 11
[15 empty] | 3CLEARNING 2TMY15WA | 3C | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,30/Dec | 29 | 13:30,18/Sep | 9
[15 empty] | 3CPERFORMANCETMY15WA | 3C | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 13:30,19/Jan | 18 | 05:30,20/Dec | 7
[15 empty] | 3CLEARNING 4TMY15WA | 3C | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,29/Oct | 30 | 13:30,18/Sep | 8
[15 empty] | 3CLEARNING 3TMY15WA | 3C | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 10:30,31/Oct | 33 | 12:30,18/Sep | 9
[15 empty] | 3CFOOD PREPTMY15WA | 3C | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 07:30,01/Feb | 40 | 11:30,20/Sep | 17
[15 empty] | 3CGYMTMY15WA | 3C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 07:30,11/Jul | 37 | 11:30,18/Sep | 10
[15 empty] | 3CADMINMIN | 3C | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 06:30,16/Jul | 30 | 04:30,01/Feb | 12
[15 empty] | 3CLEARNING 1MIN | 3C | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,09/Jul | 33 | 08:30,19/Dec | 13
[15 empty] | 3CLEARNING 2MIN | 3C | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,13/May | 29 | 04:30,11/Jan | 12
[15 empty] | 3CPERFORMANCEMIN | 3C | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 14:30,09/Nov | 26 | 04:30,06/Dec | 8
[15 empty] | 3CLEARNING 4MIN | 3C | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 06:30,03/Aug | 28 | 03:30,01/Feb | 10
[15 empty] | 3CLEARNING 3MIN | 3C | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 06:30,02/Jul | 29 | 02:30,01/Feb | 10
[15 empty] | 3CFOOD PREPMIN | 3C | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,25/Nov | 34 | 11:30,09/Sep | 13
[15 empty] | 3CGYMMIN | 3C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 10:30,15/Feb | 34 | 00:30,06/Dec | 11
[15 empty] | 3CADMINMAX | 3C | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,22/Jan | 36 | 13:30,18/Sep | 9
[15 empty] | 3CLEARNING 1MAX | 3C | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 07:30,25/Oct | 45 | 14:30,18/Sep | 11
[15 empty] | 3CLEARNING 2MAX | 3C | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,03/May | 30 | 14:30,18/Sep | 10
[15 empty] | 3CPERFORMANCEMAX | 3C | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 19:30,23/Feb | 22 | 19:30,25/Jul | 8
[15 empty] | 3CLEARNING 4MAX | 3C | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,26/Oct | 32 | 15:30,25/Jul | 9
[15 empty] | 3CLEARNING 3MAX | 3C | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 07:30,25/Oct | 34 | 13:30,18/Sep | 10
[15 empty] | 3CFOOD PREPMAX | 3C | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 07:30,15/Jan | 41 | 11:30,31/May | 21
[15 empty] | 3CGYMMAX | 3C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 07:30,14/Jan | 38 | 17:30,13/Sep | 11
[15 empty] | 4ALocationFilename | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 4AADMINTMY15WA | 4A | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,10/Mar | 56 | 15:30,25/Jul | 16
[15 empty] | 4ALEARNING 1TMY15WA | 4A | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,08/Mar | 62 | 12:30,25/Jul | 19
[15 empty] | 4ALEARNING 2TMY15WA | 4A | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,11/Nov | 52 | 15:30,25/Jul | 15
[15 empty] | 4APERFORMANCETMY15WA | 4A | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 14:30,28/Mar | 44 | 20:30,25/Jul | 12
[15 empty] | 4ALEARNING 4TMY15WA | 4A | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,14/Apr | 50 | 13:30,25/Jul | 15
[15 empty] | 4ALEARNING 3TMY15WA | 4A | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 07:30,08/Nov | 52 | 14:30,25/Jul | 16
[15 empty] | 4AFOOD PREPTMY15WA | 4A | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,21/Jan | 45 | 13:30,24/Jul | 21
[15 empty] | 4AGYMTMY15WA | 4A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 07:30,16/Dec | 43 | 10:30,24/Jul | 17
[15 empty] | 4AADMINTMY3 | 4A | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,14/Apr | 53 | 14:30,14/Aug | 16
[15 empty] | 4ALEARNING 1TMY3 | 4A | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,16/Nov | 61 | 14:30,14/Aug | 18
[15 empty] | 4ALEARNING 2TMY3 | 4A | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,16/Apr | 47 | 15:30,14/Aug | 14
[15 empty] | 4APERFORMANCETMY3 | 4A | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 19:30,01/Feb | 42 | 06:30,07/Feb | 12
[15 empty] | 4ALEARNING 4TMY3 | 4A | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,31/Mar | 46 | 12:30,14/Aug | 15
[15 empty] | 4ALEARNING 3TMY3 | 4A | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 06:30,29/Mar | 49 | 12:30,14/Aug | 16
[15 empty] | 4AFOOD PREPTMY3 | 4A | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,04/Jan | 45 | 15:30,14/Aug | 20
[15 empty] | 4AGYMTMY3 | 4A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,09/Mar | 43 | 10:30,10/Jul | 16
[15 empty] | 4AADMINTMY7WA | 4A | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 06:30,28/Oct | 56 | 15:30,25/Jul | 16
[15 empty] | 4ALEARNING 1TMY7WA | 4A | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,22/Dec | 63 | 14:30,25/Jul | 18
[15 empty] | 4ALEARNING 2TMY7WA | 4A | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,26/Nov | 52 | 15:30,25/Jul | 14
[15 empty] | 4APERFORMANCETMY7WA | 4A | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 11:30,14/Nov | 44 | 20:30,25/Jul | 12
[15 empty] | 4ALEARNING 4TMY7WA | 4A | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,27/Oct | 49 | 14:30,25/Jul | 14
[15 empty] | 4ALEARNING 3TMY7WA | 4A | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,12/Apr | 53 | 14:30,25/Jul | 16
[15 empty] | 4AFOOD PREPTMY7WA | 4A | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,22/Jan | 49 | 12:30,06/Sep | 21
[15 empty] | 4AGYMTMY7WA | 4A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 07:30,17/Nov | 43 | 10:30,24/Jul | 16
[15 empty] | 4AADMINTMY3WA | 4A | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,16/Apr | 56 | 15:30,25/Jul | 16
[15 empty] | 4ALEARNING 1TMY3WA | 4A | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,08/Mar | 63 | 14:30,25/Jul | 19
[15 empty] | 4ALEARNING 2TMY3WA | 4A | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,11/Nov | 52 | 15:30,25/Jul | 15
[15 empty] | 4APERFORMANCETMY3WA | 4A | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 09:30,19/Feb | 44 | 20:30,25/Jul | 12
[15 empty] | 4ALEARNING 4TMY3WA | 4A | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,14/Apr | 49 | 16:30,25/Jul | 15
[15 empty] | 4ALEARNING 3TMY3WA | 4A | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 10:30,09/May | 52 | 14:30,25/Jul | 16
[15 empty] | 4AFOOD PREPTMY3WA | 4A | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 07:30,01/Feb | 46 | 15:30,25/Jul | 22
[15 empty] | 4AGYMTMY3WA | 4A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 09:30,28/Jan | 43 | 10:30,24/Jul | 17
[15 empty] | 4AADMINTMY2 | 4A | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 06:30,06/Apr | 51 | 11:30,25/Jul | 16
[15 empty] | 4ALEARNING 1TMY2 | 4A | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,24/Nov | 63 | 11:30,25/Jul | 18
[15 empty] | 4ALEARNING 2TMY2 | 4A | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,23/Apr | 44 | 14:30,25/Jul | 14
[15 empty] | 4APERFORMANCETMY2 | 4A | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 07:30,02/Apr | 43 | 05:30,18/Jan | 12
[15 empty] | 4ALEARNING 4TMY2 | 4A | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,30/Apr | 45 | 11:30,25/Jul | 15
[15 empty] | 4ALEARNING 3TMY2 | 4A | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 07:30,10/May | 47 | 15:30,18/Jul | 16
[15 empty] | 4AFOOD PREPTMY2 | 4A | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,05/Jan | 44 | 14:30,11/Jul | 19
[15 empty] | 4AGYMTMY2 | 4A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 14:30,04/Jan | 43 | 20:30,17/Jan | 16
[15 empty] | 4AADMINMIN | 4A | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 06:30,01/Jun | 40 | 04:30,11/Jan | 16
[15 empty] | 4ALEARNING 1MIN | 4A | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,25/May | 47 | 18:30,01/Aug | 17
[15 empty] | 4ALEARNING 2MIN | 4A | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,21/Oct | 36 | 07:30,24/Jan | 14
[15 empty] | 4APERFORMANCEMIN | 4A | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 20:30,17/May | 42 | 01:30,17/Jan | 12
[15 empty] | 4ALEARNING 4MIN | 4A | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,30/Sep | 37 | 03:30,11/Jan | 14
[15 empty] | 4ALEARNING 3MIN | 4A | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 12:30,18/Nov | 39 | 07:30,24/Jan | 15
[15 empty] | 4AFOOD PREPMIN | 4A | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,23/Nov | 40 | 17:30,16/Jul | 16
[15 empty] | 4AGYMMIN | 4A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 08:30,26/Oct | 42 | 03:30,25/Jan | 15
[15 empty] | 4AADMINMAX | 4A | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,22/Nov | 58 | 13:30,01/Aug | 19
[15 empty] | 4ALEARNING 1MAX | 4A | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 07:30,30/Dec | 64 | 13:30,31/Jul | 22
[15 empty] | 4ALEARNING 2MAX | 4A | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,28/Jan | 54 | 14:30,01/Aug | 17
[15 empty] | 4APERFORMANCEMAX | 4A | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 17:30,22/Feb | 47 | 20:30,25/Jul | 14
[15 empty] | 4ALEARNING 4MAX | 4A | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,09/Dec | 51 | 14:30,31/Jul | 17
[15 empty] | 4ALEARNING 3MAX | 4A | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 11:30,04/Apr | 54 | 13:30,01/Aug | 19
[15 empty] | 4AFOOD PREPMAX | 4A | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 07:30,10/Feb | 46 | 12:30,31/May | 26
[15 empty] | 4AGYMMAX | 4A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 07:30,28/Jan | 44 | 10:30,31/Jul | 19
[15 empty] | 4BLocationFilename | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 4BADMINTMY7WA | 4B | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 06:30,26/Apr | 44 | 13:30,18/Jul | 14
[15 empty] | 4BLEARNING 1TMY7WA | 4B | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 06:30,10/Jun | 50 | 13:30,18/Jul | 16
[15 empty] | 4BLEARNING 2TMY7WA | 4B | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,20/Apr | 39 | 14:30,18/Jul | 13
[15 empty] | 4BPERFORMANCETMY7WA | 4B | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 19:30,01/Nov | 40 | 03:30,27/Dec | 10
[15 empty] | 4BLEARNING 4TMY7WA | 4B | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,22/Apr | 38 | 13:30,18/Jul | 13
[15 empty] | 4BLEARNING 3TMY7WA | 4B | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,18/May | 41 | 13:30,18/Jul | 14
[15 empty] | 4BFOOD PREPTMY7WA | 4B | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,28/Jan | 44 | 13:30,20/Jul | 17
[15 empty] | 4BGYMTMY7WA | 4B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 14:30,21/Dec | 40 | 10:30,17/Jul | 15
[15 empty] | 4BADMINTMY3WA | 4B | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,27/Oct | 44 | 13:30,01/Aug | 14
[15 empty] | 4BLEARNING 1TMY3WA | 4B | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 06:30,08/Jun | 52 | 14:30,01/Aug | 16
[15 empty] | 4BLEARNING 2TMY3WA | 4B | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,11/Mar | 40 | 14:30,01/Aug | 13
[15 empty] | 4BPERFORMANCETMY3WA | 4B | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 07:30,28/Apr | 40 | 02:30,29/Nov | 10
[15 empty] | 4BLEARNING 4TMY3WA | 4B | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,25/Mar | 42 | 13:30,11/Jul | 13
[15 empty] | 4BLEARNING 3TMY3WA | 4B | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 07:30,06/May | 42 | 13:30,01/Aug | 14
[15 empty] | 4BFOOD PREPTMY3WA | 4B | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 06:30,01/Mar | 41 | 11:30,03/Sep | 17
[15 empty] | 4BGYMTMY3WA | 4B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 08:30,19/Feb | 40 | 10:30,03/Jul | 15
[15 empty] | 4BADMINTMY3 | 4B | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 09:30,09/May | 46 | 15:30,21/Aug | 15
[15 empty] | 4BLEARNING 1TMY3 | 4B | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 06:30,14/May | 53 | 15:30,21/Aug | 17
[15 empty] | 4BLEARNING 2TMY3 | 4B | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,21/Apr | 41 | 15:30,21/Aug | 13
[15 empty] | 4BPERFORMANCETMY3 | 4B | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 13:30,10/Nov | 34 | 05:30,13/Dec | 11
[15 empty] | 4BLEARNING 4TMY3 | 4B | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,14/Apr | 38 | 14:30,25/Jul | 14
[15 empty] | 4BLEARNING 3TMY3 | 4B | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 07:30,10/May | 42 | 15:30,21/Aug | 14
[15 empty] | 4BFOOD PREPTMY3 | 4B | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,18/Jan | 41 | 11:30,03/Sep | 17
[15 empty] | 4BGYMTMY3 | 4B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 15:30,29/Jan | 39 | 11:30,14/Aug | 15
[15 empty] | 4BADMINTMY2 | 4B | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 06:30,11/May | 46 | 14:30,01/Aug | 15
[15 empty] | 4BLEARNING 1TMY2 | 4B | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 06:30,12/May | 53 | 14:30,01/Aug | 17
[15 empty] | 4BLEARNING 2TMY2 | 4B | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,26/Oct | 42 | 16:30,01/Aug | 13
[15 empty] | 4BPERFORMANCETMY2 | 4B | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 14:30,03/Nov | 38 | 05:30,04/Jan | 11
[15 empty] | 4BLEARNING 4TMY2 | 4B | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,03/May | 40 | 15:30,01/Aug | 14
[15 empty] | 4BLEARNING 3TMY2 | 4B | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 07:30,17/May | 42 | 19:30,02/Aug | 15
[15 empty] | 4BFOOD PREPTMY2 | 4B | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,31/Dec | 41 | 11:30,03/Sep | 17
[15 empty] | 4BGYMTMY2 | 4B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 15:30,26/Nov | 40 | 11:30,10/Jul | 15
[15 empty] | 4BADMINTMY15WA | 4B | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,28/Apr | 44 | 13:30,18/Jul | 14
[15 empty] | 4BLEARNING 1TMY15WA | 4B | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 06:30,19/May | 51 | 14:30,28/Aug | 16
[15 empty] | 4BLEARNING 2TMY15WA | 4B | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,15/Apr | 39 | 14:30,18/Jul | 13
[15 empty] | 4BPERFORMANCETMY15WA | 4B | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 12:30,19/Nov | 40 | 02:30,29/Nov | 10
[15 empty] | 4BLEARNING 4TMY15WA | 4B | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,27/Apr | 38 | 14:30,21/Aug | 13
[15 empty] | 4BLEARNING 3TMY15WA | 4B | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 09:30,02/May | 41 | 13:30,18/Jul | 14
[15 empty] | 4BFOOD PREPTMY15WA | 4B | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,05/Jan | 44 | 13:30,20/Jul | 17
[15 empty] | 4BGYMTMY15WA | 4B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,15/Mar | 40 | 10:30,17/Jul | 15
[15 empty] | 4BADMINMIN | 4B | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,16/Jun | 44 | 04:30,03/Feb | 16
[15 empty] | 4BLEARNING 1MIN | 4B | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,09/Jun | 50 | 04:30,03/Feb | 18
[15 empty] | 4BLEARNING 2MIN | 4B | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,24/Sep | 39 | 04:30,03/Feb | 15
[15 empty] | 4BPERFORMANCEMIN | 4B | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 17:30,07/Oct | 43 | 05:30,03/Feb | 12
[15 empty] | 4BLEARNING 4MIN | 4B | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,16/Jun | 40 | 04:30,03/Feb | 15
[15 empty] | 4BLEARNING 3MIN | 4B | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 07:30,16/Jun | 43 | 04:30,03/Feb | 15
[15 empty] | 4BFOOD PREPMIN | 4B | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,29/Oct | 39 | 17:30,31/Jul | 15
[15 empty] | 4BGYMMIN | 4B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 14:30,18/Mar | 42 | 01:30,18/Jan | 15
[15 empty] | 4BADMINMAX | 4B | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 10:30,11/Apr | 46 | 13:30,18/Jul | 14
[15 empty] | 4BLEARNING 1MAX | 4B | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,19/May | 52 | 13:30,28/Aug | 17
[15 empty] | 4BLEARNING 2MAX | 4B | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,04/Mar | 41 | 14:30,18/Jul | 13
[15 empty] | 4BPERFORMANCEMAX | 4B | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 14:30,11/Feb | 37 | 19:30,18/Jul | 10
[15 empty] | 4BLEARNING 4MAX | 4B | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,19/Apr | 41 | 13:30,18/Jul | 13
[15 empty] | 4BLEARNING 3MAX | 4B | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 10:30,16/Oct | 43 | 13:30,18/Jul | 14
[15 empty] | 4BFOOD PREPMAX | 4B | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 08:30,14/Dec | 45 | 13:30,14/Jul | 18
[15 empty] | 4BGYMMAX | 4B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 15:30,01/Jan | 40 | 11:30,03/Jul | 15
[15 empty] | 4CLocationFilename | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 4CADMINTMY7WA | 4C | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 06:30,23/Jun | 47 | 14:30,31/Jul | 13
[15 empty] | 4CLEARNING 1TMY7WA | 4C | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,29/Sep | 54 | 16:30,31/Jul | 14
[15 empty] | 4CLEARNING 2TMY7WA | 4C | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,25/Mar | 41 | 15:30,31/Jul | 12
[15 empty] | 4CPERFORMANCETMY7WA | 4C | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 14:30,11/Feb | 35 | 05:30,04/Jan | 9
[15 empty] | 4CLEARNING 4TMY7WA | 4C | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,06/Oct | 39 | 15:30,31/Jul | 11
[15 empty] | 4CLEARNING 3TMY7WA | 4C | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 08:30,06/Jun | 43 | 13:30,31/Jul | 12
[15 empty] | 4CFOOD PREPTMY7WA | 4C | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 06:30,22/Mar | 46 | 13:30,29/Jul | 16
[15 empty] | 4CGYMTMY7WA | 4C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 08:30,09/Nov | 40 | 11:30,31/Jul | 13
[15 empty] | 4CADMINTMY3WA | 4C | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,17/Jun | 38 | 14:30,14/Aug | 12
[15 empty] | 4CLEARNING 1TMY3WA | 4C | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 06:30,15/Sep | 49 | 16:30,14/Aug | 13
[15 empty] | 4CLEARNING 2TMY3WA | 4C | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,09/Apr | 34 | 15:30,14/Aug | 11
[15 empty] | 4CPERFORMANCETMY3WA | 4C | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 09:30,07/May | 29 | 05:30,31/Dec | 8
[15 empty] | 4CLEARNING 4TMY3WA | 4C | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,04/Oct | 34 | 15:30,14/Aug | 10
[15 empty] | 4CLEARNING 3TMY3WA | 4C | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 09:30,29/Aug | 34 | 18:30,12/Jul | 11
[15 empty] | 4CFOOD PREPTMY3WA | 4C | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 07:30,01/Nov | 39 | 12:30,21/Sep | 16
[15 empty] | 4CGYMTMY3WA | 4C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 08:30,15/Dec | 38 | 17:30,21/Sep | 12
[15 empty] | 4CADMINTMY3 | 4C | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,20/Oct | 37 | 19:30,21/Jul | 12
[15 empty] | 4CLEARNING 1TMY3 | 4C | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,23/Nov | 53 | 18:30,21/Jul | 14
[15 empty] | 4CLEARNING 2TMY3 | 4C | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,19/Mar | 37 | 18:30,21/Jul | 11
[15 empty] | 4CPERFORMANCETMY3 | 4C | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 11:30,11/Apr | 27 | 05:30,25/Jan | 9
[15 empty] | 4CLEARNING 4TMY3 | 4C | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,06/Oct | 35 | 19:30,21/Jul | 11
[15 empty] | 4CLEARNING 3TMY3 | 4C | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 11:30,20/Jun | 40 | 19:30,21/Jul | 12
[15 empty] | 4CFOOD PREPTMY3 | 4C | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 06:30,08/Feb | 40 | 17:30,21/Jul | 17
[15 empty] | 4CGYMTMY3 | 4C | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 07:30,24/Mar | 40 | 17:30,09/Sep | 12
[15 empty] | 4CADMINTMY2 | 4C | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 11:30,06/Jun | 36 | 14:30,15/Aug | 12
[15 empty] | 4CLEARNING 1TMY2 | 4C | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,20/Jan | 46 | 17:30,09/Sep | 14
[15 empty] | 4CLEARNING 2TMY2 | 4C | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,23/Apr | 32 | 18:30,10/Sep | 11
[15 empty] | 4CPERFORMANCETMY2 | 4C | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 13:30,18/Jan | 36 | 06:30,31/Jan | 8
[15 empty] | 4CLEARNING 4TMY2 | 4C | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,04/Oct | 32 | 15:30,24/Jul | 11
[15 empty] | 4CLEARNING 3TMY2 | 4C | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 07:30,04/Oct | 37 | 18:30,09/Sep | 12
[15 empty] | 4CFOOD PREPTMY2 | 4C | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,29/Jan | 39 | 13:30,10/Sep | 16
[15 empty] | 4CGYMTMY2 | 4C | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 07:30,24/Mar | 40 | 17:30,09/Sep | 12
[15 empty] | 4CADMINTMY15WA | 4C | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,23/Jun | 47 | 14:30,31/Jul | 12
[15 empty] | 4CLEARNING 1TMY15WA | 4C | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,29/Sep | 54 | 16:30,31/Jul | 14
[15 empty] | 4CLEARNING 2TMY15WA | 4C | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,23/Apr | 41 | 15:30,31/Jul | 11
[15 empty] | 4CPERFORMANCETMY15WA | 4C | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 11:30,31/Jan | 29 | 05:30,31/Dec | 8
[15 empty] | 4CLEARNING 4TMY15WA | 4C | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 12:30,20/Jun | 39 | 15:30,31/Jul | 11
[15 empty] | 4CLEARNING 3TMY15WA | 4C | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 09:30,23/May | 43 | 13:30,31/Jul | 12
[15 empty] | 4CFOOD PREPTMY15WA | 4C | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 07:30,08/Feb | 46 | 13:30,29/Jul | 16
[15 empty] | 4CGYMTMY15WA | 4C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,15/Dec | 40 | 11:30,31/Jul | 12
[15 empty] | 4CADMINMIN | 4C | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,13/Jul | 37 | 07:30,07/Feb | 15
[15 empty] | 4CLEARNING 1MIN | 4C | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,18/Aug | 40 | 04:30,08/Dec | 16
[15 empty] | 4CLEARNING 2MIN | 4C | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,20/May | 33 | 06:30,07/Feb | 14
[15 empty] | 4CPERFORMANCEMIN | 4C | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 09:30,24/Sep | 41 | 05:30,06/Jan | 10
[15 empty] | 4CLEARNING 4MIN | 4C | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,03/Aug | 34 | 07:30,07/Feb | 13
[15 empty] | 4CLEARNING 3MIN | 4C | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 11:30,07/Aug | 36 | 07:30,07/Feb | 14
[15 empty] | 4CFOOD PREPMIN | 4C | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,29/Nov | 33 | 11:30,13/Sep | 12
[15 empty] | 4CGYMMIN | 4C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 15:30,18/Nov | 40 | 00:30,06/Dec | 14
[15 empty] | 4CADMINMAX | 4C | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,28/Oct | 51 | 15:30,31/Jul | 14
[15 empty] | 4CLEARNING 1MAX | 4C | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,17/Jun | 56 | 15:30,11/Sep | 15
[15 empty] | 4CLEARNING 2MAX | 4C | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,26/Oct | 43 | 16:30,31/Jul | 12
[15 empty] | 4CPERFORMANCEMAX | 4C | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 20:30,01/Dec | 33 | 20:30,15/Aug | 9
[15 empty] | 4CLEARNING 4MAX | 4C | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,20/Apr | 40 | 16:30,31/Jul | 12
[15 empty] | 4CLEARNING 3MAX | 4C | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 10:30,25/Apr | 44 | 15:30,31/Jul | 13
[15 empty] | 4CFOOD PREPMAX | 4C | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 08:30,02/Feb | 43 | 13:30,29/Jul | 19
[15 empty] | 4CGYMMAX | 4C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 07:30,25/Feb | 41 | 11:30,24/Jul | 13
[15 empty] | 5ALocationFilename | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 5AADMINTMY15WA | 5A | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 04:30,18/Oct | 50 | 12:30,24/Jul | 16
[15 empty] | 5ALEARNING 1TMY15WA | 5A | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,24/Feb | 61 | 15:30,14/Aug | 18
[15 empty] | 5ALEARNING 2TMY15WA | 5A | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,03/Nov | 46 | 16:30,14/Aug | 14
[15 empty] | 5APERFORMANCETMY15WA | 5A | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 17:30,23/Nov | 39 | 05:30,05/Dec | 12
[15 empty] | 5ALEARNING 4TMY15WA | 5A | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,05/Apr | 45 | 12:30,24/Jul | 14
[15 empty] | 5ALEARNING 3TMY15WA | 5A | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 05:30,18/Oct | 49 | 15:30,14/Aug | 16
[15 empty] | 5AFOOD PREPTMY15WA | 5A | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,04/Feb | 43 | 16:30,14/Aug | 19
[15 empty] | 5AGYMTMY15WA | 5A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 07:30,22/Apr | 42 | 10:30,24/Jul | 16
[15 empty] | 5AADMINTMY7WA | 5A | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 05:30,03/May | 50 | 12:30,24/Jul | 16
[15 empty] | 5ALEARNING 1TMY7WA | 5A | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,08/Nov | 61 | 15:30,14/Aug | 18
[15 empty] | 5ALEARNING 2TMY7WA | 5A | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,20/Oct | 46 | 16:30,14/Aug | 14
[15 empty] | 5APERFORMANCETMY7WA | 5A | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 07:30,09/Nov | 42 | 05:30,23/Jan | 12
[15 empty] | 5ALEARNING 4TMY7WA | 5A | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,18/Oct | 45 | 12:30,24/Jul | 14
[15 empty] | 5ALEARNING 3TMY7WA | 5A | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,11/May | 49 | 15:30,14/Aug | 16
[15 empty] | 5AFOOD PREPTMY7WA | 5A | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,16/Feb | 43 | 12:30,24/Jul | 19
[15 empty] | 5AGYMTMY7WA | 5A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 07:30,05/Nov | 42 | 10:30,24/Jul | 16
[15 empty] | 5AADMINTMY3WA | 5A | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 04:30,18/Oct | 52 | 13:30,14/Aug | 15
[15 empty] | 5ALEARNING 1TMY3WA | 5A | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,14/Apr | 60 | 11:30,14/Aug | 17
[15 empty] | 5ALEARNING 2TMY3WA | 5A | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,25/Nov | 47 | 14:30,14/Aug | 14
[15 empty] | 5APERFORMANCETMY3WA | 5A | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 17:30,23/Nov | 39 | 05:30,05/Dec | 11
[15 empty] | 5ALEARNING 4TMY3WA | 5A | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,03/Nov | 44 | 12:30,14/Aug | 14
[15 empty] | 5ALEARNING 3TMY3WA | 5A | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 05:30,18/Oct | 48 | 12:30,14/Aug | 15
[15 empty] | 5AFOOD PREPTMY3WA | 5A | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 08:30,18/Jan | 43 | 13:30,17/Jul | 20
[15 empty] | 5AGYMTMY3WA | 5A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 07:30,22/Apr | 42 | 10:30,14/Aug | 16
[15 empty] | 5AADMINTMY3 | 5A | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,18/May | 52 | 14:30,18/Jul | 16
[15 empty] | 5ALEARNING 1TMY3 | 5A | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,21/Oct | 61 | 13:30,18/Jul | 18
[15 empty] | 5ALEARNING 2TMY3 | 5A | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,11/Mar | 47 | 16:30,18/Jul | 14
[15 empty] | 5APERFORMANCETMY3 | 5A | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 18:30,11/Mar | 43 | 03:30,28/Jan | 12
[15 empty] | 5ALEARNING 4TMY3 | 5A | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,30/Apr | 45 | 13:30,18/Jul | 15
[15 empty] | 5ALEARNING 3TMY3 | 5A | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 05:30,27/Sep | 48 | 15:30,18/Jul | 16
[15 empty] | 5AFOOD PREPTMY3 | 5A | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,28/Dec | 43 | 11:30,17/Jul | 18
[15 empty] | 5AGYMTMY3 | 5A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,19/Mar | 43 | 03:30,20/Dec | 16
[15 empty] | 5AADMINTMY2 | 5A | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 06:30,18/May | 46 | 14:30,03/Jul | 16
[15 empty] | 5ALEARNING 1TMY2 | 5A | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,01/Apr | 58 | 13:30,03/Jul | 18
[15 empty] | 5ALEARNING 2TMY2 | 5A | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,23/Apr | 42 | 14:30,03/Jul | 14
[15 empty] | 5APERFORMANCETMY2 | 5A | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 12:30,23/Nov | 43 | 03:30,28/Jan | 12
[15 empty] | 5ALEARNING 4TMY2 | 5A | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,28/Oct | 41 | 13:30,03/Jul | 14
[15 empty] | 5ALEARNING 3TMY2 | 5A | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 05:30,27/Sep | 46 | 20:30,04/Aug | 15
[15 empty] | 5AFOOD PREPTMY2 | 5A | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,04/Jan | 43 | 17:30,04/Aug | 18
[15 empty] | 5AGYMTMY2 | 5A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,11/Nov | 41 | 10:30,03/Jul | 16
[15 empty] | 5AADMINMIN | 5A | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,10/Jun | 43 | 06:30,31/Jan | 16
[15 empty] | 5ALEARNING 1MIN | 5A | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,10/Jun | 45 | 06:30,31/Jan | 18
[15 empty] | 5ALEARNING 2MIN | 5A | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,30/Sep | 38 | 06:30,31/Jan | 15
[15 empty] | 5APERFORMANCEMIN | 5A | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 09:30,29/Sep | 43 | 01:30,07/Jan | 12
[15 empty] | 5ALEARNING 4MIN | 5A | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,16/Sep | 39 | 05:30,31/Jan | 15
[15 empty] | 5ALEARNING 3MIN | 5A | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 11:30,01/Nov | 41 | 05:30,31/Jan | 16
[15 empty] | 5AFOOD PREPMIN | 5A | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,23/Mar | 37 | 11:30,09/Aug | 15
[15 empty] | 5AGYMMIN | 5A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 07:30,13/May | 44 | 02:30,01/Feb | 15
[15 empty] | 5AADMINMAX | 5A | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,04/Nov | 54 | 13:30,01/Aug | 17
[15 empty] | 5ALEARNING 1MAX | 5A | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,04/Nov | 61 | 12:30,18/Jul | 19
[15 empty] | 5ALEARNING 2MAX | 5A | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,25/Feb | 49 | 14:30,01/Aug | 15
[15 empty] | 5APERFORMANCEMAX | 5A | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 07:30,22/Nov | 46 | 21:30,25/Jul | 12
[15 empty] | 5ALEARNING 4MAX | 5A | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 12:30,28/Mar | 47 | 15:30,07/Aug | 15
[15 empty] | 5ALEARNING 3MAX | 5A | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 12:30,11/Apr | 50 | 15:30,08/Aug | 17
[15 empty] | 5AFOOD PREPMAX | 5A | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 08:30,18/Jan | 45 | 12:30,01/Sep | 23
[15 empty] | 5AGYMMAX | 5A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 07:30,06/Jan | 42 | 10:30,17/Jul | 17
[15 empty] | 5BLocationFilename | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 5BADMINTMY7WA | 5B | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 07:30,21/Jun | 41 | 05:30,06/Feb | 15
[15 empty] | 5BLEARNING 1TMY7WA | 5B | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 06:30,12/Aug | 45 | 05:30,06/Feb | 16
[15 empty] | 5BLEARNING 2TMY7WA | 5B | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,27/May | 36 | 03:30,07/Feb | 14
[15 empty] | 5BPERFORMANCETMY7WA | 5B | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 07:30,15/Sep | 42 | 02:30,06/Feb | 11
[15 empty] | 5BLEARNING 4TMY7WA | 5B | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 06:30,22/Jun | 37 | 05:30,06/Feb | 13
[15 empty] | 5BLEARNING 3TMY7WA | 5B | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,22/Jun | 39 | 06:30,06/Feb | 14
[15 empty] | 5BFOOD PREPTMY7WA | 5B | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,30/Dec | 38 | 13:30,19/Jul | 14
[15 empty] | 5BGYMTMY7WA | 5B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 14:30,02/Dec | 40 | 04:30,08/Feb | 14
[15 empty] | 5BADMINTMY3WA | 5B | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,17/Jun | 39 | 03:30,24/Dec | 14
[15 empty] | 5BLEARNING 1TMY3WA | 5B | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 06:30,12/Aug | 45 | 14:30,31/Jul | 16
[15 empty] | 5BLEARNING 2TMY3WA | 5B | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,29/Apr | 35 | 04:30,24/Dec | 14
[15 empty] | 5BPERFORMANCETMY3WA | 5B | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 14:30,23/Mar | 41 | 05:30,23/Dec | 10
[15 empty] | 5BLEARNING 4TMY3WA | 5B | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 06:30,07/Jun | 36 | 04:30,24/Dec | 13
[15 empty] | 5BLEARNING 3TMY3WA | 5B | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 06:30,17/Jun | 37 | 04:30,24/Dec | 14
[15 empty] | 5BFOOD PREPTMY3WA | 5B | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 08:30,01/Feb | 38 | 13:30,19/Jul | 14
[15 empty] | 5BGYMTMY3WA | 5B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 15:30,09/Nov | 39 | 22:30,17/Jan | 14
[15 empty] | 5BADMINTMY3 | 5B | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,04/Jun | 42 | 04:30,13/Dec | 14
[15 empty] | 5BLEARNING 1TMY3 | 5B | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 06:30,04/Jun | 46 | 14:30,26/Jun | 16
[15 empty] | 5BLEARNING 2TMY3 | 5B | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,08/Apr | 38 | 04:30,13/Dec | 13
[15 empty] | 5BPERFORMANCETMY3 | 5B | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 07:30,04/Nov | 42 | 06:30,11/Dec | 10
[15 empty] | 5BLEARNING 4TMY3 | 5B | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,14/Oct | 39 | 04:30,13/Dec | 13
[15 empty] | 5BLEARNING 3TMY3 | 5B | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 07:30,26/Oct | 40 | 04:30,13/Dec | 14
[15 empty] | 5BFOOD PREPTMY3 | 5B | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,26/Nov | 39 | 13:30,09/Sep | 16
[15 empty] | 5BGYMTMY3 | 5B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 08:30,10/Feb | 43 | 23:30,12/Dec | 14
[15 empty] | 5BADMINTMY2 | 5B | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 06:30,04/Jun | 42 | 04:30,13/Dec | 14
[15 empty] | 5BLEARNING 1TMY2 | 5B | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 06:30,04/Jun | 47 | 13:30,18/Jul | 16
[15 empty] | 5BLEARNING 2TMY2 | 5B | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,14/May | 38 | 03:30,13/Dec | 13
[15 empty] | 5BPERFORMANCETMY2 | 5B | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 11:30,16/May | 42 | 06:30,11/Dec | 10
[15 empty] | 5BLEARNING 4TMY2 | 5B | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 06:30,04/Jun | 39 | 02:30,13/Dec | 13
[15 empty] | 5BLEARNING 3TMY2 | 5B | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 07:30,07/May | 40 | 03:30,13/Dec | 14
[15 empty] | 5BFOOD PREPTMY2 | 5B | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,30/Nov | 39 | 17:30,22/Jul | 16
[15 empty] | 5BGYMTMY2 | 5B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 15:30,13/Jan | 43 | 23:30,12/Dec | 14
[15 empty] | 5BADMINTMY15WA | 5B | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,16/Jun | 39 | 02:30,24/Dec | 14
[15 empty] | 5BLEARNING 1TMY15WA | 5B | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 06:30,26/Aug | 44 | 14:30,25/Jul | 16
[15 empty] | 5BLEARNING 2TMY15WA | 5B | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,22/Apr | 35 | 03:30,24/Dec | 13
[15 empty] | 5BPERFORMANCETMY15WA | 5B | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 14:30,23/Apr | 41 | 05:30,23/Dec | 10
[15 empty] | 5BLEARNING 4TMY15WA | 5B | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 06:30,26/Aug | 36 | 03:30,24/Dec | 13
[15 empty] | 5BLEARNING 3TMY15WA | 5B | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 07:30,05/May | 37 | 03:30,24/Dec | 14
[15 empty] | 5BFOOD PREPTMY15WA | 5B | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,11/Feb | 38 | 11:30,03/Sep | 14
[15 empty] | 5BGYMTMY15WA | 5B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,01/Nov | 40 | 02:30,18/Jan | 14
[15 empty] | 5BADMINMIN | 5B | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,05/Jul | 45 | 03:30,02/Feb | 19
[15 empty] | 5BLEARNING 1MIN | 5B | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,06/Aug | 49 | 04:30,02/Feb | 20
[15 empty] | 5BLEARNING 2MIN | 5B | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,12/Jul | 40 | 02:30,06/Dec | 17
[15 empty] | 5BPERFORMANCEMIN | 5B | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 13:30,27/Jun | 43 | 02:30,02/Feb | 14
[15 empty] | 5BLEARNING 4MIN | 5B | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,13/Aug | 41 | 03:30,06/Dec | 17
[15 empty] | 5BLEARNING 3MIN | 5B | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 11:30,04/Jul | 43 | 04:30,02/Feb | 18
[15 empty] | 5BFOOD PREPMIN | 5B | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,12/May | 36 | 13:30,19/Jul | 14
[15 empty] | 5BGYMMIN | 5B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 14:30,21/Apr | 46 | 04:30,06/Dec | 17
[15 empty] | 5BADMINMAX | 5B | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,29/Sep | 33 | 04:30,27/Dec | 13
[15 empty] | 5BLEARNING 1MAX | 5B | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,15/Jun | 44 | 16:30,25/Jul | 15
[15 empty] | 5BLEARNING 2MAX | 5B | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,26/Oct | 31 | 15:30,25/Jul | 12
[15 empty] | 5BPERFORMANCEMAX | 5B | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 14:30,12/Mar | 27 | 05:30,27/Dec | 9
[15 empty] | 5BLEARNING 4MAX | 5B | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,06/May | 34 | 14:30,03/Jul | 12
[15 empty] | 5BLEARNING 3MAX | 5B | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 10:30,09/May | 33 | 15:30,31/Jul | 13
[15 empty] | 5BFOOD PREPMAX | 5B | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 08:30,24/Dec | 40 | 11:30,06/Sep | 16
[15 empty] | 5BGYMMAX | 5B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 09:30,15/Nov | 37 | 17:30,06/Sep | 14
[15 empty] | 5CLocationFilename | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 5CADMINTMY7WA | 5C | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 16:30,29/Aug | 31 | 04:30,04/Jan | 12
[15 empty] | 5CLEARNING 1TMY7WA | 5C | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,01/Jun | 36 | 18:30,30/Jun | 13
[15 empty] | 5CLEARNING 2TMY7WA | 5C | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,15/Apr | 28 | 04:30,04/Jan | 11
[15 empty] | 5CPERFORMANCETMY7WA | 5C | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 19:30,02/Nov | 26 | 05:30,31/Dec | 8
[15 empty] | 5CLEARNING 4TMY7WA | 5C | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,06/Oct | 29 | 00:30,01/Feb | 10
[15 empty] | 5CLEARNING 3TMY7WA | 5C | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 10:30,12/Sep | 30 | 23:30,31/Jan | 12
[15 empty] | 5CFOOD PREPTMY7WA | 5C | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,30/Dec | 38 | 11:30,08/Sep | 15
[15 empty] | 5CGYMTMY7WA | 5C | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 08:30,28/Jan | 34 | 21:30,31/Jan | 12
[15 empty] | 5CADMINTMY3WA | 5C | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,03/Jun | 36 | 14:30,15/Aug | 11
[15 empty] | 5CLEARNING 1TMY3WA | 5C | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,18/May | 43 | 18:30,27/Jul | 13
[15 empty] | 5CLEARNING 2TMY3WA | 5C | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,09/Apr | 30 | 18:30,27/Jul | 11
[15 empty] | 5CPERFORMANCETMY3WA | 5C | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 12:30,03/Oct | 23 | 05:30,29/Dec | 8
[15 empty] | 5CLEARNING 4TMY3WA | 5C | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,12/Apr | 31 | 16:30,25/Jul | 10
[15 empty] | 5CLEARNING 3TMY3WA | 5C | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 13:30,02/May | 34 | 19:30,27/Jul | 11
[15 empty] | 5CFOOD PREPTMY3WA | 5C | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 07:30,01/Nov | 39 | 13:30,28/Jul | 16
[15 empty] | 5CGYMTMY3WA | 5C | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 08:30,09/Dec | 36 | 17:30,28/Jul | 11
[15 empty] | 5CADMINTMY15WA | 5C | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,21/Jun | 37 | 13:30,11/Jul | 12
[15 empty] | 5CLEARNING 1TMY15WA | 5C | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,28/Apr | 48 | 15:30,11/Jul | 13
[15 empty] | 5CLEARNING 2TMY15WA | 5C | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,14/Oct | 36 | 15:30,11/Jul | 11
[15 empty] | 5CPERFORMANCETMY15WA | 5C | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 17:30,11/Nov | 26 | 05:30,01/Nov | 8
[15 empty] | 5CLEARNING 4TMY15WA | 5C | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,04/Oct | 34 | 15:30,11/Jul | 10
[15 empty] | 5CLEARNING 3TMY15WA | 5C | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 07:30,31/May | 38 | 14:30,11/Jul | 11
[15 empty] | 5CFOOD PREPTMY15WA | 5C | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 07:30,08/Mar | 39 | 11:30,13/Sep | 15
[15 empty] | 5CGYMTMY15WA | 5C | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,09/Dec | 35 | 21:30,31/Oct | 11
[15 empty] | 5CADMINMAX | 5C | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,05/May | 36 | 14:30,11/Jul | 11
[15 empty] | 5CLEARNING 1MAX | 5C | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 07:30,15/Nov | 47 | 15:30,11/Jul | 13
[15 empty] | 5CLEARNING 2MAX | 5C | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,12/Feb | 35 | 16:30,11/Jul | 11
[15 empty] | 5CPERFORMANCEMAX | 5C | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 18:30,30/Mar | 26 | 19:30,11/Jul | 8
[15 empty] | 5CLEARNING 4MAX | 5C | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,12/Apr | 36 | 14:30,11/Jul | 10
[15 empty] | 5CLEARNING 3MAX | 5C | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 11:30,09/May | 37 | 15:30,11/Jul | 12
[15 empty] | 5CFOOD PREPMAX | 5C | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 6 | 07:30,01/Mar | 39 | 11:30,30/Jul | 18
[15 empty] | 5CGYMMAX | 5C | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 07:30,02/Apr | 38 | 13:30,24/Jul | 12
[15 empty] | 5CADMINMIN | 5C | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,09/Jul | 40 | 03:30,20/Dec | 15
[15 empty] | 5CLEARNING 1MIN | 5C | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,23/Aug | 42 | 04:30,20/Dec | 16
[15 empty] | 5CLEARNING 2MIN | 5C | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,04/Jun | 35 | 03:30,20/Dec | 13
[15 empty] | 5CPERFORMANCEMIN | 5C | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 10:30,02/Oct | 41 | 05:30,20/Dec | 10
[15 empty] | 5CLEARNING 4MIN | 5C | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,01/Jul | 37 | 03:30,20/Dec | 13
[15 empty] | 5CLEARNING 3MIN | 5C | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 07:30,01/Jul | 39 | 04:30,20/Dec | 14
[15 empty] | 5CFOOD PREPMIN | 5C | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,09/Mar | 34 | 12:30,02/Sep | 13
[15 empty] | 5CGYMMIN | 5C | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 14:30,05/Nov | 42 | 00:30,20/Dec | 14
[15 empty] | 5CADMINdoeCWEC | 5C | People dissatisfied | ADMIN | doeCWEC | Percentage (%) | 5 | 07:30,21/Jun | 35 | 03:30,22/Nov | 12
[15 empty] | 5CLEARNING 1doeCWEC | 5C | People dissatisfied | LEARNING 1 | doeCWEC | Percentage (%) | 5 | 07:30,21/Jun | 37 | 03:30,22/Nov | 14
[15 empty] | 5CLEARNING 2doeCWEC | 5C | People dissatisfied | LEARNING 2 | doeCWEC | Percentage (%) | 5 | 07:30,23/Apr | 31 | 03:30,22/Nov | 11
[15 empty] | 5CPERFORMANCEdoeCWEC | 5C | People dissatisfied | PERFORMANCE | doeCWEC | Percentage (%) | 5 | 14:30,02/Apr | 31 | 05:30,22/Nov | 8
[15 empty] | 5CLEARNING 4doeCWEC | 5C | People dissatisfied | LEARNING 4 | doeCWEC | Percentage (%) | 5 | 07:30,22/Oct | 32 | 03:30,22/Nov | 11
[15 empty] | 5CLEARNING 3doeCWEC | 5C | People dissatisfied | LEARNING 3 | doeCWEC | Percentage (%) | 5 | 09:30,27/Jun | 34 | 02:30,22/Nov | 12
[15 empty] | 5CFOOD PREPdoeCWEC | 5C | People dissatisfied | FOOD PREP | doeCWEC | Percentage (%) | 5 | 08:30,22/Nov | 38 | 11:30,02/Sep | 15
[15 empty] | 5CGYMdoeCWEC | 5C | People dissatisfied | GYM | doeCWEC | Percentage (%) | 5 | 15:30,04/Mar | 36 | 00:30,22/Nov | 12
[15 empty] | 5CADMINCWEC | 5C | People dissatisfied | ADMIN | CWEC | Percentage (%) | 5 | 07:30,21/Jun | 35 | 03:30,22/Nov | 12
[15 empty] | 5CLEARNING 1CWEC | 5C | People dissatisfied | LEARNING 1 | CWEC | Percentage (%) | 5 | 07:30,21/Jun | 37 | 02:30,22/Nov | 13
[15 empty] | 5CLEARNING 2CWEC | 5C | People dissatisfied | LEARNING 2 | CWEC | Percentage (%) | 5 | 07:30,23/Apr | 32 | 04:30,22/Nov | 11
[15 empty] | 5CPERFORMANCECWEC | 5C | People dissatisfied | PERFORMANCE | CWEC | Percentage (%) | 5 | 15:30,16/May | 31 | 05:30,22/Nov | 8
[15 empty] | 5CLEARNING 4CWEC | 5C | People dissatisfied | LEARNING 4 | CWEC | Percentage (%) | 5 | 07:30,20/Oct | 32 | 04:30,22/Nov | 11
[15 empty] | 5CLEARNING 3CWEC | 5C | People dissatisfied | LEARNING 3 | CWEC | Percentage (%) | 5 | 07:30,29/Apr | 34 | 02:30,22/Nov | 12
[15 empty] | 5CFOOD PREPCWEC | 5C | People dissatisfied | FOOD PREP | CWEC | Percentage (%) | 5 | 08:30,22/Nov | 38 | 11:30,02/Sep | 15
[15 empty] | 5CGYMCWEC | 5C | People dissatisfied | GYM | CWEC | Percentage (%) | 5 | 15:30,04/Mar | 36 | 00:30,22/Nov | 12
[15 empty] | 6ALocationFilename | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 6AADMINTMY7WA | 6A | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 02:30,03/May | 51 | 13:30,08/Aug | 16
[15 empty] | 6ALEARNING 1TMY7WA | 6A | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,24/Mar | 59 | 12:30,08/Aug | 18
[15 empty] | 6ALEARNING 2TMY7WA | 6A | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,02/Apr | 44 | 13:30,08/Aug | 15
[15 empty] | 6APERFORMANCETMY7WA | 6A | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 13:30,17/Oct | 42 | 01:30,01/Feb | 12
[15 empty] | 6ALEARNING 4TMY7WA | 6A | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,14/Oct | 44 | 14:30,08/Aug | 15
[15 empty] | 6ALEARNING 3TMY7WA | 6A | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,10/May | 46 | 13:30,08/Aug | 16
[15 empty] | 6AFOOD PREPTMY7WA | 6A | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,23/Nov | 45 | 07:30,04/Jul | 18
[15 empty] | 6AGYMTMY7WA | 6A | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 10:30,08/Nov | 43 | 17:30,24/Jan | 16
[15 empty] | 6AADMINTMY3WA | 6A | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,04/May | 55 | 13:30,18/Jul | 16
[15 empty] | 6ALEARNING 1TMY3WA | 6A | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,21/Oct | 64 | 13:30,18/Jul | 18
[15 empty] | 6ALEARNING 2TMY3WA | 6A | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,04/Nov | 48 | 15:30,18/Jul | 14
[15 empty] | 6APERFORMANCETMY3WA | 6A | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 13:30,09/Nov | 42 | 03:30,05/Dec | 11
[15 empty] | 6ALEARNING 4TMY3WA | 6A | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 07:30,30/Sep | 47 | 14:30,18/Jul | 14
[15 empty] | 6ALEARNING 3TMY3WA | 6A | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 09:30,06/Nov | 48 | 12:30,18/Jul | 15
[15 empty] | 6AFOOD PREPTMY3WA | 6A | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 08:30,19/Jan | 45 | 14:30,31/Jul | 19
[15 empty] | 6AGYMTMY3WA | 6A | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 08:30,25/Oct | 43 | 10:30,31/Jul | 16
[15 empty] | 6AADMINTMY3 | 6A | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,28/Sep | 49 | 20:30,18/Jul | 17
[15 empty] | 6ALEARNING 1TMY3 | 6A | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,13/May | 61 | 12:30,04/Jul | 19
[15 empty] | 6ALEARNING 2TMY3 | 6A | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,05/May | 44 | 18:30,18/Jul | 15
[15 empty] | 6APERFORMANCETMY3 | 6A | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 10:30,18/Nov | 44 | 01:30,31/Jan | 12
[15 empty] | 6ALEARNING 4TMY3 | 6A | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,07/May | 43 | 13:30,04/Jul | 15
[15 empty] | 6ALEARNING 3TMY3 | 6A | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 13:30,01/Dec | 46 | 20:30,05/Jul | 16
[15 empty] | 6AFOOD PREPTMY3 | 6A | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,10/Feb | 45 | 13:30,20/Jul | 18
[15 empty] | 6AGYMTMY3 | 6A | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 15:30,25/Mar | 44 | 04:30,01/Feb | 16
[15 empty] | 6AADMINTMY2 | 6A | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 06:30,16/Apr | 46 | 15:30,18/Jul | 17
[15 empty] | 6ALEARNING 1TMY2 | 6A | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,01/Apr | 57 | 15:30,17/Jul | 18
[15 empty] | 6ALEARNING 2TMY2 | 6A | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,21/Oct | 40 | 15:30,18/Jul | 15
[15 empty] | 6APERFORMANCETMY2 | 6A | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 10:30,02/Oct | 43 | 03:30,07/Jan | 12
[15 empty] | 6ALEARNING 4TMY2 | 6A | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,15/Apr | 41 | 12:30,17/Jul | 15
[15 empty] | 6ALEARNING 3TMY2 | 6A | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 07:30,15/Apr | 44 | 20:30,16/Jul | 16
[15 empty] | 6AFOOD PREPTMY2 | 6A | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,24/Dec | 42 | 17:30,16/Jul | 18
[15 empty] | 6AGYMTMY2 | 6A | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,31/Mar | 44 | 01:30,08/Feb | 16
[15 empty] | 6AADMINTMY15WA | 6A | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,08/Oct | 53 | 14:30,04/Jul | 16
[15 empty] | 6ALEARNING 1TMY15WA | 6A | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,24/Nov | 62 | 15:30,03/Jul | 18
[15 empty] | 6ALEARNING 2TMY15WA | 6A | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,05/Oct | 48 | 15:30,04/Jul | 15
[15 empty] | 6APERFORMANCETMY15WA | 6A | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 13:30,09/Nov | 42 | 03:30,20/Jan | 12
[15 empty] | 6ALEARNING 4TMY15WA | 6A | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,13/Apr | 46 | 15:30,03/Jul | 15
[15 empty] | 6ALEARNING 3TMY15WA | 6A | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 09:30,06/Nov | 47 | 14:30,03/Jul | 16
[15 empty] | 6AFOOD PREPTMY15WA | 6A | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,16/Mar | 44 | 19:30,24/Jul | 19
[15 empty] | 6AGYMTMY15WA | 6A | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 07:30,06/Apr | 42 | 10:30,17/Jul | 16
[15 empty] | 6AADMINMIN | 6A | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,23/Aug | 45 | 04:30,01/Feb | 18
[15 empty] | 6ALEARNING 1MIN | 6A | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 06:30,18/Aug | 49 | 04:30,21/Jan | 19
[15 empty] | 6ALEARNING 2MIN | 6A | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,17/Jun | 41 | 04:30,01/Feb | 16
[15 empty] | 6APERFORMANCEMIN | 6A | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 15:30,12/Sep | 44 | 07:30,31/Jan | 13
[15 empty] | 6ALEARNING 4MIN | 6A | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,17/Jun | 41 | 04:30,01/Feb | 16
[15 empty] | 6ALEARNING 3MIN | 6A | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 06:30,18/Aug | 43 | 04:30,01/Feb | 17
[15 empty] | 6AFOOD PREPMIN | 6A | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,20/Apr | 37 | 13:30,30/Jul | 16
[15 empty] | 6AGYMMIN | 6A | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 15:30,05/Oct | 46 | 04:30,01/Feb | 16
[15 empty] | 6AADMINMAX | 6A | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,05/Apr | 57 | 14:30,18/Jul | 18
[15 empty] | 6ALEARNING 1MAX | 6A | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,21/Oct | 65 | 12:30,18/Jul | 20
[15 empty] | 6ALEARNING 2MAX | 6A | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,19/Nov | 54 | 15:30,18/Jul | 16
[15 empty] | 6APERFORMANCEMAX | 6A | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 18:30,24/Nov | 48 | 19:30,18/Jul | 13
[15 empty] | 6ALEARNING 4MAX | 6A | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 06:30,05/Apr | 51 | 15:30,18/Jul | 16
[15 empty] | 6ALEARNING 3MAX | 6A | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 13:30,24/Oct | 53 | 14:30,18/Jul | 18
[15 empty] | 6AFOOD PREPMAX | 6A | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 08:30,01/Jan | 46 | 12:30,01/Sep | 22
[15 empty] | 6AGYMMAX | 6A | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 08:30,25/Feb | 42 | 14:30,03/Jul | 18
[15 empty] | 6BLocationFilename | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 6BADMINTMY7WA | 6B | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 10 | 06:30,19/Jan | 58 | 14:30,04/Apr | 30
[15 empty] | 6BLEARNING 1TMY7WA | 6B | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 8 | 06:30,19/Jan | 65 | 13:30,08/May | 36
[15 empty] | 6BLEARNING 2TMY7WA | 6B | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 8 | 06:30,19/Jan | 53 | 14:30,22/May | 25
[15 empty] | 6BPERFORMANCETMY7WA | 6B | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 13 | 07:30,19/Jan | 47 | 13:30,03/Sep | 23
[15 empty] | 6BLEARNING 4TMY7WA | 6B | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 9 | 07:30,19/Jan | 50 | 15:30,04/Apr | 27
[15 empty] | 6BLEARNING 3TMY7WA | 6B | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 8 | 06:30,19/Jan | 53 | 21:30,05/Apr | 29
[15 empty] | 6BFOOD PREPTMY7WA | 6B | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 14 | 06:30,19/Jan | 70 | 12:30,03/Sep | 36
[15 empty] | 6BGYMTMY7WA | 6B | People dissatisfied | GYM | TMY7WA | Percentage (%) | 10 | 06:30,19/Jan | 62 | 13:30,03/Sep | 31
[15 empty] | 6BADMINTMY3WA | 6B | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,16/Jun | 42 | 14:30,25/Jul | 15
[15 empty] | 6BLEARNING 1TMY3WA | 6B | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 06:30,07/Jun | 50 | 16:30,25/Jul | 17
[15 empty] | 6BLEARNING 2TMY3WA | 6B | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,30/Jun | 37 | 16:30,25/Jul | 14
[15 empty] | 6BPERFORMANCETMY3WA | 6B | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 07:30,30/Apr | 39 | 05:30,04/Jan | 10
[15 empty] | 6BLEARNING 4TMY3WA | 6B | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 06:30,16/Jun | 37 | 15:30,25/Jul | 13
[15 empty] | 6BLEARNING 3TMY3WA | 6B | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 06:30,16/Jun | 40 | 15:30,25/Jul | 14
[15 empty] | 6BFOOD PREPTMY3WA | 6B | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 08:30,07/Dec | 39 | 11:30,21/Jul | 14
[15 empty] | 6BGYMTMY3WA | 6B | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 15:30,11/Feb | 39 | 00:30,01/Mar | 15
[15 empty] | 6BADMINTMY3 | 6B | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 06:30,02/Jun | 42 | 23:30,26/Dec | 15
[15 empty] | 6BLEARNING 1TMY3 | 6B | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 06:30,02/Jun | 45 | 23:30,26/Dec | 16
[15 empty] | 6BLEARNING 2TMY3 | 6B | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,21/Oct | 38 | 00:30,27/Dec | 14
[15 empty] | 6BPERFORMANCETMY3 | 6B | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 07:30,21/Apr | 42 | 02:30,25/Feb | 10
[15 empty] | 6BLEARNING 4TMY3 | 6B | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 06:30,03/Jun | 39 | 23:30,26/Dec | 13
[15 empty] | 6BLEARNING 3TMY3 | 6B | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 06:30,02/Jun | 41 | 00:30,27/Dec | 14
[15 empty] | 6BFOOD PREPTMY3 | 6B | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,15/Feb | 39 | 11:30,01/Sep | 15
[15 empty] | 6BGYMTMY3 | 6B | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 14:30,26/Nov | 43 | 02:30,27/Dec | 14
[15 empty] | 6BADMINTMY2 | 6B | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 07:30,07/Jun | 44 | 07:30,12/Dec | 15
[15 empty] | 6BLEARNING 1TMY2 | 6B | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 06:30,02/Sep | 48 | 05:30,12/Dec | 17
[15 empty] | 6BLEARNING 2TMY2 | 6B | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,31/Mar | 40 | 06:30,12/Dec | 14
[15 empty] | 6BPERFORMANCETMY2 | 6B | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 10:30,08/May | 43 | 07:30,12/Dec | 10
[15 empty] | 6BLEARNING 4TMY2 | 6B | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,08/Jun | 41 | 04:30,12/Dec | 13
[15 empty] | 6BLEARNING 3TMY2 | 6B | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 12:30,05/Sep | 42 | 05:30,12/Dec | 14
[15 empty] | 6BFOOD PREPTMY2 | 6B | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,08/Mar | 38 | 13:30,30/Jun | 15
[15 empty] | 6BGYMTMY2 | 6B | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,04/Oct | 44 | 04:30,18/Jan | 15
[15 empty] | 6BADMINTMY15WA | 6B | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,14/Jun | 37 | 04:30,30/Dec | 15
[15 empty] | 6BLEARNING 1TMY15WA | 6B | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 06:30,26/Aug | 45 | 15:30,24/Jul | 16
[15 empty] | 6BLEARNING 2TMY15WA | 6B | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,18/Jun | 34 | 04:30,30/Dec | 14
[15 empty] | 6BPERFORMANCETMY15WA | 6B | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 07:30,30/Apr | 41 | 05:30,30/Dec | 10
[15 empty] | 6BLEARNING 4TMY15WA | 6B | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 06:30,25/Jun | 34 | 04:30,30/Dec | 13
[15 empty] | 6BLEARNING 3TMY15WA | 6B | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 07:30,22/Jun | 36 | 04:30,30/Dec | 14
[15 empty] | 6BFOOD PREPTMY15WA | 6B | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,29/Jan | 39 | 11:30,03/Sep | 14
[15 empty] | 6BGYMTMY15WA | 6B | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 15:30,28/Oct | 37 | 04:30,08/Mar | 14
[15 empty] | 6BADMINMIN | 6B | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,19/Jul | 45 | 04:30,17/Feb | 19
[15 empty] | 6BLEARNING 1MIN | 6B | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,20/Jul | 50 | 04:30,17/Feb | 21
[15 empty] | 6BLEARNING 2MIN | 6B | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,20/Aug | 40 | 01:30,20/Dec | 18
[15 empty] | 6BPERFORMANCEMIN | 6B | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 15:30,30/Aug | 44 | 03:30,18/Feb | 14
[15 empty] | 6BLEARNING 4MIN | 6B | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,26/Jul | 41 | 04:30,06/Dec | 17
[15 empty] | 6BLEARNING 3MIN | 6B | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 12:30,25/Jul | 43 | 04:30,18/Feb | 18
[15 empty] | 6BFOOD PREPMIN | 6B | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,12/Apr | 33 | 13:30,28/Jul | 14
[15 empty] | 6BGYMMIN | 6B | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 15:30,15/Oct | 46 | 03:30,06/Dec | 18
[15 empty] | 6BADMINMAX | 6B | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,07/Oct | 42 | 13:30,01/Aug | 14
[15 empty] | 6BLEARNING 1MAX | 6B | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,18/May | 49 | 18:30,16/Jul | 16
[15 empty] | 6BLEARNING 2MAX | 6B | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,15/Oct | 37 | 13:30,01/Aug | 13
[15 empty] | 6BPERFORMANCEMAX | 6B | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 10:30,12/Nov | 30 | 20:30,18/Jul | 9
[15 empty] | 6BLEARNING 4MAX | 6B | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,12/May | 36 | 13:30,18/Jul | 13
[15 empty] | 6BLEARNING 3MAX | 6B | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 07:30,24/May | 39 | 14:30,18/Jul | 14
[15 empty] | 6BFOOD PREPMAX | 6B | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 08:30,25/Feb | 45 | 13:30,12/Jul | 16
[15 empty] | 6BGYMMAX | 6B | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 10:30,11/Mar | 37 | 12:30,24/Jul | 14
[15 empty] | 7LocationFilename | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 7ADMINTMY7WA | 7 | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 22:30,19/Sep | 43 | 14:30,03/Jul | 16
[15 empty] | 7LEARNING 1TMY7WA | 7 | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 06:30,30/Sep | 54 | 15:30,03/Jul | 17
[15 empty] | 7LEARNING 2TMY7WA | 7 | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,30/Apr | 38 | 15:30,03/Jul | 14
[15 empty] | 7PERFORMANCETMY7WA | 7 | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 20:30,01/Jun | 43 | 00:30,03/Jan | 11
[15 empty] | 7LEARNING 4TMY7WA | 7 | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,17/Sep | 39 | 04:30,04/Jan | 14
[15 empty] | 7LEARNING 3TMY7WA | 7 | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,01/Jun | 40 | 04:30,04/Jan | 15
[15 empty] | 7FOOD PREPTMY7WA | 7 | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,29/Mar | 46 | 13:30,14/Jul | 17
[15 empty] | 7GYMTMY7WA | 7 | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 08:30,03/Nov | 43 | 03:30,04/Jan | 15
[15 empty] | 7ADMINTMY3WA | 7 | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,05/Oct | 49 | 13:30,04/Jul | 15
[15 empty] | 7LEARNING 1TMY3WA | 7 | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,15/Nov | 59 | 15:30,04/Jul | 17
[15 empty] | 7LEARNING 2TMY3WA | 7 | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,14/May | 45 | 15:30,04/Jul | 14
[15 empty] | 7PERFORMANCETMY3WA | 7 | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 11:30,16/Oct | 42 | 06:30,05/Dec | 11
[15 empty] | 7LEARNING 4TMY3WA | 7 | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 06:30,05/May | 42 | 15:30,04/Jul | 13
[15 empty] | 7LEARNING 3TMY3WA | 7 | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 07:30,04/May | 46 | 14:30,04/Jul | 14
[15 empty] | 7FOOD PREPTMY3WA | 7 | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 08:30,27/Dec | 43 | 11:30,31/May | 17
[15 empty] | 7GYMTMY3WA | 7 | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 08:30,12/Oct | 41 | 10:30,03/Jul | 15
[15 empty] | 7ADMINTMY3 | 7 | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 07:30,03/Jun | 48 | 14:30,17/Jul | 16
[15 empty] | 7LEARNING 1TMY3 | 7 | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,07/Jun | 58 | 14:30,17/Jul | 17
[15 empty] | 7LEARNING 2TMY3 | 7 | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,14/May | 41 | 14:30,17/Jul | 15
[15 empty] | 7PERFORMANCETMY3 | 7 | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 09:30,15/May | 44 | 04:30,20/Dec | 12
[15 empty] | 7LEARNING 4TMY3 | 7 | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 07:30,24/Sep | 40 | 03:30,20/Dec | 14
[15 empty] | 7LEARNING 3TMY3 | 7 | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 10:30,23/May | 43 | 14:30,17/Jul | 15
[15 empty] | 7FOOD PREPTMY3 | 7 | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,25/Nov | 41 | 18:30,26/Jun | 16
[15 empty] | 7GYMTMY3 | 7 | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 14:30,27/Oct | 45 | 04:30,20/Dec | 15
[15 empty] | 7ADMINTMY2 | 7 | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 07:30,25/Jun | 45 | 04:30,08/Feb | 16
[15 empty] | 7LEARNING 1TMY2 | 7 | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,02/Jun | 50 | 17:30,11/Jul | 18
[15 empty] | 7LEARNING 2TMY2 | 7 | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,21/Oct | 41 | 04:30,08/Feb | 15
[15 empty] | 7PERFORMANCETMY2 | 7 | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 17:30,08/Nov | 44 | 05:30,02/Feb | 12
[15 empty] | 7LEARNING 4TMY2 | 7 | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,24/Jun | 41 | 04:30,08/Feb | 15
[15 empty] | 7LEARNING 3TMY2 | 7 | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 10:30,13/Jun | 43 | 04:30,08/Feb | 15
[15 empty] | 7FOOD PREPTMY2 | 7 | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,22/Feb | 44 | 13:30,12/Jul | 16
[15 empty] | 7GYMTMY2 | 7 | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 08:30,11/Oct | 46 | 04:30,01/Feb | 15
[15 empty] | 7ADMINTMY15WA | 7 | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 06:30,07/May | 51 | 13:30,18/Jul | 15
[15 empty] | 7LEARNING 1TMY15WA | 7 | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,15/Nov | 63 | 12:30,18/Jul | 17
[15 empty] | 7LEARNING 2TMY15WA | 7 | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,07/Oct | 46 | 15:30,18/Jul | 14
[15 empty] | 7PERFORMANCETMY15WA | 7 | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 08:30,24/Apr | 41 | 05:30,02/Jan | 11
[15 empty] | 7LEARNING 4TMY15WA | 7 | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 07:30,13/Apr | 44 | 13:30,18/Jul | 14
[15 empty] | 7LEARNING 3TMY15WA | 7 | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 07:30,06/May | 46 | 13:30,18/Jul | 15
[15 empty] | 7FOOD PREPTMY15WA | 7 | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,05/Feb | 43 | 12:30,01/Jul | 17
[15 empty] | 7GYMTMY15WA | 7 | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 08:30,30/Mar | 42 | 10:30,17/Jul | 15
[15 empty] | 7ADMINMIN | 7 | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 07:30,02/Jul | 46 | 07:30,17/Jan | 18
[15 empty] | 7LEARNING 1MIN | 7 | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,02/Jul | 50 | 07:30,17/Jan | 20
[15 empty] | 7LEARNING 2MIN | 7 | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,20/Aug | 42 | 07:30,17/Jan | 17
[15 empty] | 7PERFORMANCEMIN | 7 | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 14:30,27/May | 45 | 05:30,18/Jan | 13
[15 empty] | 7LEARNING 4MIN | 7 | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,25/Aug | 42 | 18:30,17/Jan | 16
[15 empty] | 7LEARNING 3MIN | 7 | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 20:30,15/Aug | 44 | 08:30,17/Jan | 17
[15 empty] | 7FOOD PREPMIN | 7 | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,09/Apr | 36 | 13:30,19/Jul | 15
[15 empty] | 7GYMMIN | 7 | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 06:30,13/Aug | 46 | 04:30,15/Feb | 17
[15 empty] | 7ADMINMAX | 7 | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,27/Apr | 56 | 14:30,18/Jul | 16
[15 empty] | 7LEARNING 1MAX | 7 | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,30/Sep | 64 | 13:30,18/Jul | 19
[15 empty] | 7LEARNING 2MAX | 7 | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,09/Apr | 50 | 14:30,18/Jul | 15
[15 empty] | 7PERFORMANCEMAX | 7 | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 11:30,06/Apr | 44 | 20:30,18/Jul | 12
[15 empty] | 7LEARNING 4MAX | 7 | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,03/Nov | 47 | 13:30,18/Jul | 15
[15 empty] | 7LEARNING 3MAX | 7 | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 07:30,26/Apr | 50 | 13:30,18/Jul | 16
[15 empty] | 7FOOD PREPMAX | 7 | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 08:30,01/Jan | 44 | 17:30,18/Jul | 20
[15 empty] | 7GYMMAX | 7 | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 07:30,30/Mar | 41 | 11:30,24/Jul | 16
[15 empty] | 8LocationFilename | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | 8ADMINTMY15WA | 8 | People dissatisfied | ADMIN | TMY15WA | Percentage (%) | 5 | 07:30,10/Aug | 44 | 15:30,27/Jun | 17
[15 empty] | 8LEARNING 1TMY15WA | 8 | People dissatisfied | LEARNING 1 | TMY15WA | Percentage (%) | 5 | 07:30,09/Aug | 48 | 16:30,19/Jun | 19
[15 empty] | 8LEARNING 2TMY15WA | 8 | People dissatisfied | LEARNING 2 | TMY15WA | Percentage (%) | 5 | 07:30,22/Sep | 38 | 07:30,21/Feb | 16
[15 empty] | 8PERFORMANCETMY15WA | 8 | People dissatisfied | PERFORMANCE | TMY15WA | Percentage (%) | 5 | 10:30,22/Sep | 43 | 04:30,08/Jan | 12
[15 empty] | 8LEARNING 4TMY15WA | 8 | People dissatisfied | LEARNING 4 | TMY15WA | Percentage (%) | 5 | 06:30,11/Aug | 38 | 07:30,21/Feb | 15
[15 empty] | 8LEARNING 3TMY15WA | 8 | People dissatisfied | LEARNING 3 | TMY15WA | Percentage (%) | 5 | 11:30,22/Aug | 40 | 06:30,21/Feb | 16
[15 empty] | 8FOOD PREPTMY15WA | 8 | People dissatisfied | FOOD PREP | TMY15WA | Percentage (%) | 5 | 08:30,19/Nov | 39 | 13:30,28/Jun | 16
[15 empty] | 8GYMTMY15WA | 8 | People dissatisfied | GYM | TMY15WA | Percentage (%) | 5 | 07:30,24/May | 43 | 04:30,29/Nov | 16
[15 empty] | 8ADMINTMY7WA | 8 | People dissatisfied | ADMIN | TMY7WA | Percentage (%) | 5 | 06:30,15/Jun | 45 | 04:30,27/Jan | 17
[15 empty] | 8LEARNING 1TMY7WA | 8 | People dissatisfied | LEARNING 1 | TMY7WA | Percentage (%) | 5 | 07:30,20/Aug | 50 | 04:30,27/Jan | 18
[15 empty] | 8LEARNING 2TMY7WA | 8 | People dissatisfied | LEARNING 2 | TMY7WA | Percentage (%) | 5 | 07:30,30/Apr | 41 | 04:30,28/Jan | 16
[15 empty] | 8PERFORMANCETMY7WA | 8 | People dissatisfied | PERFORMANCE | TMY7WA | Percentage (%) | 5 | 19:30,01/Sep | 45 | 05:30,28/Jan | 12
[15 empty] | 8LEARNING 4TMY7WA | 8 | People dissatisfied | LEARNING 4 | TMY7WA | Percentage (%) | 5 | 07:30,24/Aug | 41 | 04:30,27/Jan | 15
[15 empty] | 8LEARNING 3TMY7WA | 8 | People dissatisfied | LEARNING 3 | TMY7WA | Percentage (%) | 5 | 07:30,19/May | 43 | 04:30,27/Jan | 16
[15 empty] | 8FOOD PREPTMY7WA | 8 | People dissatisfied | FOOD PREP | TMY7WA | Percentage (%) | 5 | 08:30,19/Nov | 37 | 11:30,07/Sep | 15
[15 empty] | 8GYMTMY7WA | 8 | People dissatisfied | GYM | TMY7WA | Percentage (%) | 5 | 07:30,01/Sep | 44 | 02:30,25/Jan | 16
[15 empty] | 8ADMINTMY3WA | 8 | People dissatisfied | ADMIN | TMY3WA | Percentage (%) | 5 | 06:30,17/May | 44 | 15:30,31/Jul | 16
[15 empty] | 8LEARNING 1TMY3WA | 8 | People dissatisfied | LEARNING 1 | TMY3WA | Percentage (%) | 5 | 07:30,27/Aug | 48 | 16:30,31/Jul | 18
[15 empty] | 8LEARNING 2TMY3WA | 8 | People dissatisfied | LEARNING 2 | TMY3WA | Percentage (%) | 5 | 07:30,06/May | 40 | 23:30,05/Dec | 15
[15 empty] | 8PERFORMANCETMY3WA | 8 | People dissatisfied | PERFORMANCE | TMY3WA | Percentage (%) | 5 | 09:30,03/May | 43 | 23:30,05/Dec | 11
[15 empty] | 8LEARNING 4TMY3WA | 8 | People dissatisfied | LEARNING 4 | TMY3WA | Percentage (%) | 5 | 06:30,21/May | 40 | 02:30,06/Dec | 15
[15 empty] | 8LEARNING 3TMY3WA | 8 | People dissatisfied | LEARNING 3 | TMY3WA | Percentage (%) | 5 | 12:30,09/May | 42 | 23:30,05/Dec | 15
[15 empty] | 8FOOD PREPTMY3WA | 8 | People dissatisfied | FOOD PREP | TMY3WA | Percentage (%) | 5 | 08:30,26/Feb | 39 | 13:30,28/Jun | 15
[15 empty] | 8GYMTMY3WA | 8 | People dissatisfied | GYM | TMY3WA | Percentage (%) | 5 | 07:30,17/Sep | 44 | 19:30,05/Dec | 16
[15 empty] | 8ADMINTMY3 | 8 | People dissatisfied | ADMIN | TMY3 | Percentage (%) | 5 | 07:30,02/Jun | 45 | 04:30,01/Mar | 17
[15 empty] | 8LEARNING 1TMY3 | 8 | People dissatisfied | LEARNING 1 | TMY3 | Percentage (%) | 5 | 07:30,20/Aug | 49 | 04:30,12/Jan | 19
[15 empty] | 8LEARNING 2TMY3 | 8 | People dissatisfied | LEARNING 2 | TMY3 | Percentage (%) | 5 | 07:30,11/May | 41 | 03:30,01/Mar | 16
[15 empty] | 8PERFORMANCETMY3 | 8 | People dissatisfied | PERFORMANCE | TMY3 | Percentage (%) | 5 | 18:30,13/Sep | 45 | 03:30,01/Mar | 13
[15 empty] | 8LEARNING 4TMY3 | 8 | People dissatisfied | LEARNING 4 | TMY3 | Percentage (%) | 5 | 06:30,01/Jun | 42 | 04:30,01/Mar | 16
[15 empty] | 8LEARNING 3TMY3 | 8 | People dissatisfied | LEARNING 3 | TMY3 | Percentage (%) | 5 | 07:30,12/May | 43 | 00:30,06/Dec | 16
[15 empty] | 8FOOD PREPTMY3 | 8 | People dissatisfied | FOOD PREP | TMY3 | Percentage (%) | 5 | 08:30,22/Mar | 37 | 13:30,30/Jun | 16
[15 empty] | 8GYMTMY3 | 8 | People dissatisfied | GYM | TMY3 | Percentage (%) | 5 | 02:30,10/Jun | 45 | 01:30,13/Dec | 16
[15 empty] | 8ADMINTMY2 | 8 | People dissatisfied | ADMIN | TMY2 | Percentage (%) | 5 | 06:30,06/Jul | 50 | 01:30,04/Jan | 18
[15 empty] | 8LEARNING 1TMY2 | 8 | People dissatisfied | LEARNING 1 | TMY2 | Percentage (%) | 5 | 07:30,31/Aug | 53 | 01:30,04/Jan | 20
[15 empty] | 8LEARNING 2TMY2 | 8 | People dissatisfied | LEARNING 2 | TMY2 | Percentage (%) | 5 | 07:30,04/Jun | 45 | 01:30,04/Jan | 17
[15 empty] | 8PERFORMANCETMY2 | 8 | People dissatisfied | PERFORMANCE | TMY2 | Percentage (%) | 5 | 15:30,12/Sep | 47 | 04:30,03/Jan | 13
[15 empty] | 8LEARNING 4TMY2 | 8 | People dissatisfied | LEARNING 4 | TMY2 | Percentage (%) | 5 | 07:30,04/Jun | 45 | 01:30,04/Jan | 16
[15 empty] | 8LEARNING 3TMY2 | 8 | People dissatisfied | LEARNING 3 | TMY2 | Percentage (%) | 5 | 06:30,25/May | 47 | 03:30,04/Jan | 17
[15 empty] | 8FOOD PREPTMY2 | 8 | People dissatisfied | FOOD PREP | TMY2 | Percentage (%) | 5 | 08:30,18/Oct | 38 | 11:30,31/May | 16
[15 empty] | 8GYMTMY2 | 8 | People dissatisfied | GYM | TMY2 | Percentage (%) | 5 | 05:30,13/Aug | 48 | 01:30,04/Jan | 17
[15 empty] | 8ADMINMIN | 8 | People dissatisfied | ADMIN | MIN | Percentage (%) | 5 | 06:30,02/Jul | 50 | 04:30,11/Jan | 21
[15 empty] | 8LEARNING 1MIN | 8 | People dissatisfied | LEARNING 1 | MIN | Percentage (%) | 5 | 07:30,12/Aug | 54 | 03:30,11/Jan | 23
[15 empty] | 8LEARNING 2MIN | 8 | People dissatisfied | LEARNING 2 | MIN | Percentage (%) | 5 | 07:30,23/Jul | 46 | 04:30,11/Jan | 19
[15 empty] | 8PERFORMANCEMIN | 8 | People dissatisfied | PERFORMANCE | MIN | Percentage (%) | 5 | 09:30,11/Jul | 47 | 04:30,18/Jan | 16
[15 empty] | 8LEARNING 4MIN | 8 | People dissatisfied | LEARNING 4 | MIN | Percentage (%) | 5 | 07:30,25/Jun | 45 | 04:30,11/Jan | 19
[15 empty] | 8LEARNING 3MIN | 8 | People dissatisfied | LEARNING 3 | MIN | Percentage (%) | 5 | 07:30,14/Jul | 47 | 04:30,11/Jan | 20
[15 empty] | 8FOOD PREPMIN | 8 | People dissatisfied | FOOD PREP | MIN | Percentage (%) | 5 | 08:30,20/Sep | 33 | 21:30,19/Dec | 16
[15 empty] | 8GYMMIN | 8 | People dissatisfied | GYM | MIN | Percentage (%) | 5 | 06:30,23/Jun | 48 | 04:30,11/Jan | 19
[15 empty] | 8ADMINMAX | 8 | People dissatisfied | ADMIN | MAX | Percentage (%) | 5 | 06:30,18/May | 46 | 14:30,03/Jul | 16
[15 empty] | 8LEARNING 1MAX | 8 | People dissatisfied | LEARNING 1 | MAX | Percentage (%) | 5 | 06:30,20/May | 49 | 16:30,26/Jun | 18
[15 empty] | 8LEARNING 2MAX | 8 | People dissatisfied | LEARNING 2 | MAX | Percentage (%) | 5 | 07:30,06/May | 38 | 16:30,26/Jun | 14
[15 empty] | 8PERFORMANCEMAX | 8 | People dissatisfied | PERFORMANCE | MAX | Percentage (%) | 5 | 15:30,26/Apr | 34 | 05:30,22/Mar | 10
[15 empty] | 8LEARNING 4MAX | 8 | People dissatisfied | LEARNING 4 | MAX | Percentage (%) | 5 | 07:30,05/May | 35 | 16:30,26/Jun | 14
[15 empty] | 8LEARNING 3MAX | 8 | People dissatisfied | LEARNING 3 | MAX | Percentage (%) | 5 | 13:30,09/May | 39 | 16:30,20/Jun | 15
[15 empty] | 8FOOD PREPMAX | 8 | People dissatisfied | FOOD PREP | MAX | Percentage (%) | 5 | 08:30,24/Mar | 42 | 12:30,27/May | 15
[15 empty] | 8GYMMAX | 8 | People dissatisfied | GYM | MAX | Percentage (%) | 5 | 08:30,07/Oct | 38 | 17:30,28/May | 15

## psa Summary of Results
| Building Area (ft2): | 211975
1A - Miami | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 106206 | 1607834 | 1102010 | 63280 | 804355 | 476112 | 0 | 102628 | 148866 | 27347 | 609959 | 4438638 | 20.9394 | max EUI | max EUI
| TMY3 DOE | 40165 | 1705052 | 1102010 | 63280 | 804355 | 486885 | 0 | 108833 | 148866 | 27347 | 609959 | 4486793 | 21.1666 | 31.0388 | 23.6787
| TMY3 WA | 40165 | 2150606 | 1102010 | 65108 | 804355 | 543555 | 0 | 137273 | 148866 | 27347 | 609959 | 5019285 | 23.6787 | min EUI | min EUI
| TMY7 WA | 71392 | 1877868 | 1102010 | 65577 | 804355 | 508855 | 0 | 119864 | 148866 | 27347 | 609959 | 4726134 | 22.2957 | 20.9394 | 20.9394
| TMY15 WA | 62409 | 1988700 | 1102010 | 65331 | 804355 | 528753 | 0 | 126938 | 148866 | 27347 | 609959 | 4854709 | 22.9023 | variance | variance
| XMY Min WA | 1963493 | 453917 | 1102010 | 66079 | 804355 | 1984407 | 0 | 28973 | 148866 | 27347 | 609959 | 6579447 | 31.0388 | 47.71% | 12.94%
| XMY Max WA | 39453 | 2420550 | 1102010 | 64192 | 804355 | 579948 | 0 | 154503 | 148866 | 27347 | 609959 | 5341224 | 25.1974
2A - Houston | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5429043 | 2928596 | 2993656 | 177640 | 2023218 | 5204701 | 0 | 186932 | 345722 | 34299 | 1228691 | 19323807 | 91.1608 | max EUI | max EUI
| TMY3 DOE | 5292256 | 2970949 | 2993656 | 179554 | 2023218 | 5243975 | 0 | 189635 | 345722 | 34299 | 1228691 | 19273264 | 90.9223 | 99.3676 | 91.1608
| TMY3 WA | 3551780 | 3535158 | 2993656 | 186049 | 2023218 | 5344202 | 0 | 225648 | 345722 | 34299 | 1228691 | 18239732 | 86.0466 | min EUI | min EUI
| TMY7 WA | 4210714 | 3258072 | 2993656 | 186368 | 2023218 | 5300963 | 0 | 207962 | 345722 | 34299 | 1228691 | 18560974 | 87.5621 | 84.3488 | 86.0466
| TMY15 WA | 4199053 | 3401048 | 2993656 | 185961 | 2023218 | 5337760 | 0 | 217088 | 345722 | 34299 | 1228691 | 18737805 | 88.3963 | variance | variance
| XMY Min WA | 8665233 | 1973829 | 2993656 | 195846 | 2023218 | 4705648 | 0 | 125989 | 345722 | 34299 | 1228691 | 21063440 | 99.3676 | 16.52% | 5.625%
| XMY Max WA | 2342041 | 4239085 | 2993656 | 183590 | 2023218 | 5447643 | 0 | 270580 | 345722 | 34299 | 1228691 | 17879834 | 84.3488
2B - Phoenix | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1328146 | 3982335 | 2993656 | 175394 | 2023218 | 2331255 | 0 | 254192 | 345722 | 34299 | 1228691 | 13468217 | 63.5368 | max EUI | max EUI
| TMY3 DOE | 1074920 | 4305481 | 2993656 | 177114 | 2023218 | 2393019 | 0 | 274818 | 345722 | 34299 | 1228691 | 13622247 | 64.2635 | 66.6416 | 64.2635
| TMY3 WA | 1012089 | 4356505 | 2993656 | 181625 | 2023218 | 2369011 | 0 | 278075 | 345722 | 34299 | 1228691 | 13594200 | 64.1311 | min EUI | min EUI
| TMY7 WA | 1091363 | 3962409 | 2993656 | 180843 | 2023218 | 2324363 | 0 | 252920 | 345722 | 34299 | 1228691 | 13208793 | 62.313 | 62.313 | 62.313
| TMY15 WA | 1096484 | 4162570 | 2993656 | 181125 | 2023218 | 2362345 | 0 | 265696 | 345722 | 34299 | 1228691 | 13465115 | 63.5222 | variance | variance
| XMY Min WA | 2822401 | 2481233 | 2993656 | 181419 | 2023218 | 2250048 | 0 | 158377 | 345722 | 34299 | 1228691 | 13290373 | 62.6978 | 6.736% | 3.035%
| XMY Max WA | 597239 | 5139998 | 2993656 | 179385 | 2023218 | 2484750 | 0 | 328085 | 345722 | 34299 | 1228691 | 14126352 | 66.6416
3A - Atlanta | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1680870 | 742847 | 1102010 | 63980 | 804355 | 501133 | 6471 | 47416 | 148866 | 27347 | 609959 | 5125295 | 24.1788 | max EUI | max EUI
| TMY3 DOE | 1525424 | 807514 | 1102010 | 65054 | 804355 | 503683 | 5930 | 51543 | 148866 | 27347 | 609959 | 5041726 | 23.7845 | 33.8515 | 24.1788
| TMY3 WA | 980295 | 967389 | 1102010 | 67970 | 804355 | 508557 | 4063 | 61748 | 148866 | 27347 | 609959 | 4672600 | 22.0432 | min EUI | min EUI
| TMY7 WA | 1294368 | 925892 | 1102010 | 68096 | 804355 | 522970 | 5261 | 59100 | 148866 | 27347 | 609959 | 4958265 | 23.3908 | 19.6786 | 22.0432
| TMY15 WA | 1096181 | 953134 | 1102010 | 67696 | 804355 | 518167 | 4481 | 60838 | 148866 | 27347 | 609959 | 4783075 | 22.5643 | variance | variance
| XMY Min WA | 3779341 | 610116 | 1102010 | 67484 | 804355 | 583014 | 14185 | 38944 | 148866 | 27347 | 609959 | 7175662 | 33.8515 | 59.59% | 8.979%
| XMY Max WA | 333742 | 1124076 | 1102010 | 68177 | 804355 | 489625 | 1413 | 71750 | 148866 | 27347 | 609959 | 4171361 | 19.6786
3B - Las Vegas | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 958632 | 1090941 | 1102010 | 62884 | 804355 | 567243 | 3781 | 69635 | 148866 | 27347 | 609959 | 4835694 | 22.8126 | max EUI | max EUI
| TMY3 DOE | 986299 | 1135181 | 1102010 | 63904 | 804355 | 576916 | 3896 | 72458 | 148866 | 27347 | 609959 | 4921232 | 23.2161 | 28.4413 | 23.3961
| TMY3 WA | 942610 | 1198205 | 1102010 | 65126 | 804355 | 590594 | 3799 | 76481 | 148866 | 27347 | 609959 | 4959393 | 23.3961 | min EUI | min EUI
| TMY7 WA | 974610 | 1118592 | 1102010 | 65081 | 804355 | 572762 | 3941 | 71400 | 148866 | 27347 | 609959 | 4888964 | 23.0639 | 22.5274 | 22.8126
| TMY15 WA | 1008302 | 1142077 | 1102010 | 65108 | 804355 | 582112 | 4083 | 72899 | 148866 | 27347 | 609959 | 4957159 | 23.3856 | variance | variance
| XMY Min WA | 2554989 | 714247 | 1102010 | 64998 | 804355 | 556644 | 9799 | 45590 | 148866 | 27347 | 609959 | 6028845 | 28.4413 | 25.47% | 2.514%
| XMY Max WA | 475247 | 1457864 | 1102010 | 64775 | 804355 | 599858 | 1861 | 93055 | 148866 | 27347 | 609959 | 4775238 | 22.5274
3C - San Francisco | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | #N/A | 327356 | 1102010 | 64750 | 804355 | 441049 | 5272 | 20895 | 148866 | 27347 | 609959 | #N/A | #N/A | max EUI | max EUI
| TMY3 DOE | #N/A | 312178 | 1102010 | 65376 | 804355 | 405841 | 4359 | 19926 | 148866 | 27347 | 609959 | #N/A | #N/A | #N/A | #N/A
| TMY3 WA | #N/A | 339774 | 1102010 | 66935 | 804355 | 382730 | 3157 | 21688 | 148866 | 27347 | 609959 | #N/A | #N/A | min EUI | min EUI
| TMY7 WA | #N/A | 294691 | 1102010 | 67750 | 804355 | 412144 | 4750 | 18810 | 148866 | 27347 | 609959 | #N/A | #N/A | #N/A | #N/A
| TMY15 WA | #N/A | 331936 | 1102010 | 67421 | 804355 | 411191 | 4083 | 21187 | 148866 | 27347 | 609959 | #N/A | #N/A | variance | variance
| XMY Min WA | #N/A | 331635 | 1102010 | 66070 | 804355 | 535526 | 8471 | 21168 | 148866 | 27347 | 609959 | #N/A | #N/A | #N/A | #N/A
| XMY Max WA | #N/A | 436790 | 1102010 | 65935 | 804355 | 390924 | 2170 | 27880 | 148866 | 27347 | 609959 | #N/A | #N/A
4A - Baltimore | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 2629975 | 693221 | 1102010 | 65590 | 804355 | 549859 | 10295 | 44248 | 148866 | 27347 | 609959 | 6075766 | 28.6627 | max EUI | max EUI
| TMY3 DOE | 2402295 | 705006 | 1102010 | 65750 | 804355 | 541316 | 9454 | 45000 | 148866 | 27347 | 609959 | 5851399 | 27.6042 | 38.4806 | 28.6627
| TMY3 WA | 1604990 | 843281 | 1102010 | 68515 | 804355 | 536816 | 6648 | 53826 | 148866 | 27347 | 609959 | 5196654 | 24.5154 | min EUI | min EUI
| TMY7 WA | 1939588 | 787773 | 1102010 | 68783 | 804355 | 540741 | 7917 | 50283 | 148866 | 27347 | 609959 | 5477663 | 25.8411 | 21.0644 | 24.5154
| TMY15 WA | 1722184 | 829202 | 1102010 | 68130 | 804355 | 539267 | 7061 | 52928 | 148866 | 27347 | 609959 | 5301350 | 25.0093 | variance | variance
| XMY Min WA | 4775686 | 554938 | 1102010 | 69648 | 804355 | 620947 | 17711 | 35422 | 148866 | 27347 | 609959 | 8156930 | 38.4806 | 63.09% | 15.02%
| XMY Max WA | 675470 | 1065002 | 1102010 | 68839 | 804355 | 502429 | 2839 | 67979 | 148866 | 27347 | 609959 | 4465136 | 21.0644
4B - Albuquerque | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 2238351 | 635443 | 1102010 | 63879 | 804355 | 532815 | 8853 | 40560 | 148866 | 27347 | 609959 | 5602479 | 26.4299 | max EUI | max EUI
| TMY3 DOE | 2051382 | 633482 | 1102010 | 64332 | 804355 | 531148 | 8161 | 40435 | 148866 | 27347 | 609959 | 5411518 | 25.529 | 37.156 | 26.8527
| TMY3 WA | 1808579 | 751574 | 1102010 | 65054 | 804355 | 546042 | 7492 | 47973 | 148866 | 27347 | 609959 | 5309292 | 25.0468 | min EUI | min EUI
| TMY7 WA | 2213399 | 719641 | 1102010 | 65156 | 804355 | 556343 | 9051 | 45935 | 148866 | 27347 | 609959 | 5692103 | 26.8527 | 22.9297 | 25.0468
| TMY15 WA | 2122663 | 732836 | 1102010 | 65158 | 804355 | 553887 | 8696 | 46777 | 148866 | 27347 | 609959 | 5612595 | 26.4776 | variance | variance
| XMY Min WA | 4535548 | 540494 | 1102010 | 65196 | 804355 | 600619 | 17208 | 34500 | 148866 | 27347 | 609959 | 7876143 | 37.156 | 55.73% | 7.074%
| XMY Max WA | 1238218 | 877960 | 1102010 | 64692 | 804355 | 535976 | 5051 | 56040 | 148866 | 27347 | 609959 | 4860515 | 22.9297
4C - Portland | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 2251753 | 428323 | 1102010 | 66495 | 804355 | 516513 | 8913 | 27340 | 148866 | 27347 | 609959 | 5381915 | 25.3894 | max EUI | max EUI
| TMY3 DOE | 2097729 | 427032 | 1102010 | 67250 | 804355 | 502591 | 8360 | 27257 | 148866 | 27347 | 609959 | 5212797 | 24.5916 | 39.2225 | 26.8083
| TMY3 WA | 1942929 | 505079 | 1102010 | 71638 | 804355 | 519772 | 7948 | 32239 | 148866 | 27347 | 609959 | 5162183 | 24.3528 | min EUI | min EUI
| TMY7 WA | 2387765 | 541472 | 1102010 | 70483 | 804355 | 556269 | 9563 | 34562 | 148866 | 27347 | 609959 | 5682692 | 26.8083 | 21.3756 | 24.3528
| TMY15 WA | 2145803 | 529266 | 1102010 | 70857 | 804355 | 538202 | 8732 | 33783 | 148866 | 27347 | 609959 | 5409221 | 25.5182 | variance | variance
| XMY Min WA | 4959737 | 473675 | 1102010 | 69853 | 804355 | 679542 | 18570 | 30235 | 148866 | 27347 | 609959 | 8314190 | 39.2225 | 72.57% | 9.985%
| XMY Max WA | 1175100 | 663062 | 1102010 | 71823 | 804355 | 491311 | 4892 | 42323 | 148866 | 27347 | 609959 | 4531089 | 21.3756
5A - Chicago | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 3255772 | 620512 | 1102010 | 65392 | 804355 | 564788 | 12627 | 39607 | 148866 | 27347 | 609959 | 6641276 | 31.3305 | max EUI | max EUI
| TMY3 DOE | 3174741 | 631849 | 1102010 | 66056 | 804355 | 559791 | 12403 | 40331 | 148866 | 27347 | 609959 | 6567749 | 30.9836 | 43.2979 | 31.3305
| TMY3 WA | 2060457 | 667529 | 1102010 | 69087 | 804355 | 522366 | 8542 | 42608 | 148866 | 27347 | 609959 | 5453167 | 25.7255 | min EUI | min EUI
| TMY7 WA | 2672051 | 652395 | 1102010 | 68738 | 804355 | 549475 | 10790 | 41642 | 148866 | 27347 | 609959 | 6077669 | 28.6716 | 22.1776 | 25.7255
| TMY15 WA | 2432937 | 671779 | 1102010 | 68630 | 804355 | 543656 | 9812 | 42880 | 148866 | 27347 | 609959 | 5852272 | 27.6083 | variance | variance
| XMY Min WA | 5823457 | 506203 | 1102010 | 67871 | 804355 | 644236 | 21409 | 32311 | 148866 | 27347 | 609959 | 9178065 | 43.2979 | 68.17% | 18.09%
| XMY Max WA | 1200427 | 791627 | 1102010 | 69607 | 804355 | 501183 | 5137 | 50529 | 148866 | 27347 | 609959 | 4701088 | 22.1776
5B - Boulder | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 2740526 | 526740 | 1102010 | 65151 | 804355 | 548817 | 10847 | 33622 | 148866 | 27347 | 609959 | 6008281 | 28.3443 | max EUI | max EUI
| TMY3 DOE | 2558800 | 526897 | 1102010 | 65421 | 804355 | 543075 | 10299 | 33632 | 148866 | 27347 | 609959 | 5820702 | 27.4594 | 48.3722 | 48.3722
| TMY3 WA | 3079790 | 537091 | 1102010 | 65757 | 804355 | 576550 | 12635 | 34282 | 148866 | 27347 | 609959 | 6388683 | 30.1389 | min EUI | min EUI
| TMY7 WA | 6883712 | 473765 | 1102010 | 66908 | 804355 | 690866 | 25619 | 30240 | 148866 | 27347 | 609959 | 10253688 | 48.3722 | 27.4594 | 27.4594
| TMY15 WA | 2991239 | 544069 | 1102010 | 65617 | 804355 | 570554 | 12293 | 34728 | 148866 | 27347 | 609959 | 6301078 | 29.7256 | variance | variance
| XMY Min WA | 6883712 | 473765 | 1102010 | 66908 | 804355 | 690866 | 25619 | 30240 | 148866 | 27347 | 609959 | 10253688 | 48.3722 | 76.16% | 76.16%
| XMY Max WA | 6883712 | 473765 | 1102010 | 66908 | 804355 | 690866 | 25619 | 30240 | 148866 | 27347 | 609959 | 10253688 | 48.3722
5C - Vancouver | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
[15 empty] | max EUI | max EUI
| CWEC | 2710076 | 282185 | 1102010 | 71215 | 804355 | 579040 | 10776 | 18012 | 148866 | 27347 | 609959 | 5753882 | 27.1442 | #N/A | #N/A
| TMY3 WA | 2083285 | 308812 | 1102010 | 71305 | 804355 | 539758 | #N/A | 19711 | 148866 | 27347 | 609959 | #N/A | #N/A | min EUI | min EUI
| TMY7 WA | 2800753 | 281469 | 1102010 | 71985 | 804355 | 589875 | 11143 | 17966 | 148866 | 27347 | 609959 | 5855769 | 27.6248 | #N/A | #N/A
| TMY15 WA | 2479795 | 291022 | 1102010 | 71902 | 804355 | 572948 | 10022 | 18576 | 148866 | 27347 | 609959 | 5526843 | 26.0731 | variance | variance
| XMY Min WA | 4918697 | 292306 | 1102010 | 70096 | 804355 | 704652 | 18109 | 18658 | 148866 | 27347 | 609959 | 8105096 | 38.2361 | #N/A | #N/A
| XMY Max WA | 1609924 | 338372 | 1102010 | 72487 | 804355 | 516872 | 6727 | 21598 | 148866 | 27347 | 609959 | 4648558 | 21.9297
6A - Minneapolis | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 4738105 | 625584 | 1102010 | 65581 | 804355 | 624659 | 17987 | 39931 | 148866 | 27347 | 609959 | 8194425 | 38.6575 | max EUI | max EUI
| TMY3 DOE | 4588532 | 624162 | 1102010 | 66358 | 804355 | 627979 | 17827 | 39840 | 148866 | 27347 | 609959 | 8047276 | 37.9633 | #N/A | #N/A
| TMY3 WA | 3040329 | 696570 | 1102010 | 69312 | 804355 | 576695 | 12397 | 44462 | 148866 | 27347 | 609959 | 6522343 | 30.7694 | min EUI | min EUI
| TMY7 WA | 4248765 | 663952 | 1102010 | 69112 | 804355 | 622037 | 16731 | 42380 | 148866 | 27347 | 609959 | 7745555 | 36.5399 | #N/A | #N/A
| TMY15 WA | 3601009 | 693063 | 1102010 | 69256 | 804355 | #N/A | 14280 | 44238 | 148866 | 27347 | 609959 | #N/A | #N/A | variance | variance
| XMY Min WA | 8230745 | 553413 | 1102010 | 68745 | 804355 | #N/A | 29825 | 35324 | 148866 | 27347 | 609959 | #N/A | #N/A | #N/A | #N/A
| XMY Max WA | 2032171 | 890299 | 1102010 | 69510 | 804355 | #N/A | 8539 | 56828 | 148866 | 27347 | 609959 | #N/A | #N/A
6B - Helena | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 4401983 | 489327 | 1102010 | 65365 | 804355 | 623154 | 16759 | 31234 | 148866 | 27347 | 609959 | 7710400 | 36.3741 | max EUI | max EUI
| TMY3 DOE | 4230935 | 485665 | 1102010 | 65928 | 804355 | 617471 | 16366 | 31000 | 148866 | 27347 | 609959 | 7529943 | 35.5228 | 59.6916 | 36.3741
| TMY3 WA | 3881298 | 591055 | 1102010 | 67579 | 804355 | 640063 | 15717 | 37727 | 148866 | 27347 | 609959 | 7316017 | 34.5136 | min EUI | min EUI
| TMY7 WA | 31861 | 1819151 | 1102010 | 66270 | 804355 | 552462 | 146 | 116116 | 148866 | 27347 | 609959 | 4668584 | 22.0242 | 22.0242 | 22.0242
| TMY15 WA | 4401983 | 489327 | 1102010 | 65365 | 804355 | 623154 | 16759 | 31234 | 148866 | 27347 | 609959 | 7710400 | 36.3741 | variance | variance
| XMY Min WA | 9097926 | 517601 | 1102010 | 67907 | 804355 | 822003 | 32083 | 33038 | 148866 | 27347 | 609959 | 12653136 | 59.6916 | 106% | 40.4%
| XMY Max WA | 2771426 | 648748 | 1102010 | 66833 | 804355 | 589130 | 11272 | 41409 | 148866 | 27347 | 609959 | 6211396 | 29.3025
7 - Duluth | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5822594 | 481583 | 1102010 | 65410 | 804355 | 679162 | 22117 | 30739 | 148866 | 27347 | 609959 | 9184183 | 43.3267 | max EUI | max EUI
| TMY3 DOE | 5525251 | 470952 | 1102010 | 66252 | 804355 | 658195 | 21220 | 30061 | 148866 | 27347 | 609959 | 8854509 | 41.7715 | 57.6854 | 43.3267
| TMY3 WA | 3531195 | 564911 | 1102010 | 70186 | 804355 | 606532 | 14402 | 36058 | 148866 | 27347 | 609959 | 6905862 | 32.5787 | min EUI | min EUI
| TMY7 WA | 4620352 | 541692 | 1102010 | 70105 | 804355 | 645336 | 18253 | 34576 | 148866 | 27347 | 609959 | 8012892 | 37.8011 | 27.9873 | 32.5787
| TMY15 WA | 3932682 | 544716 | 1102010 | 69756 | 804355 | 614699 | 15757 | 34769 | 148866 | 27347 | 609959 | 7294957 | 34.4142 | variance | variance
| XMY Min WA | 8748645 | 472967 | 1102010 | 69146 | 804355 | 792504 | 31828 | 30189 | 148866 | 27347 | 609959 | 12227857 | 57.6854 | 71.1% | 25.73%
| XMY Max WA | 2477080 | 682951 | 1102010 | 70985 | 804355 | 565034 | 10390 | 43593 | 148866 | 27347 | 609959 | 5932611 | 27.9873
8 - Fairbanks | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 8964112 | 342123 | 1102010 | 72812 | 804355 | 697411 | 32917 | 21838 | 148866 | 27347 | 609959 | 12213791 | 57.619 | max EUI | max EUI
| TMY3 DOE | 8142450 | 348897 | 1102010 | 73251 | 804355 | 674940 | 30522 | 22270 | 148866 | 27347 | 609959 | 11374908 | 53.6616 | 76.7336 | 57.619
| TMY3 WA | 6058976 | 404317 | 1102010 | 74037 | 804355 | 634529 | 24181 | 25807 | 148866 | 27347 | 609959 | 9304425 | 43.894 | min EUI | min EUI
| TMY7 WA | 7466205 | 377413 | 1102010 | 74073 | 804355 | 674019 | 29036 | 24090 | 148866 | 27347 | 609959 | 10727414 | 50.607 | 36.8796 | 43.894
| TMY15 WA | 6868634 | 394543 | 1102010 | 74199 | 804355 | 654583 | 26806 | 25184 | 148866 | 27347 | 609959 | 10126527 | 47.7723 | variance | variance
| XMY Min WA | 12822837 | 367884 | 1102010 | 75106 | 804355 | 847910 | 45801 | 23482 | 148866 | 27347 | 609959 | 16265598 | 76.7336 | 74.27% | 25.58%
| XMY Max WA | 4565103 | 456842 | 1102010 | 73843 | 804355 | 590799 | 19221 | 29160 | 148866 | 27347 | 609959 | 7817546 | 36.8796
1A - Miami
2A - Houston
2B - Phoenix
3A - Atlanta
3B - Las Vegas
3C - San Francisco
4A - Baltimore
4B - Albuquerque
4C - Portland
5A - Chicago
5B - Boulder
5C - Vancouver
6A - Minneapolis
6B - Helena
7 - Duluth
8 - Fairbanks

## psa Additional Indicators
[14 empty] | Predicted Percentage Dissatisfied | [9 empty] | Peak Heating Load | [9 empty] | Peak Cooling Load
Climate Zone | Climate File | PPD - Floor 1 | PPD - Floor 2 | PPD - Kitchen | PPD - Gym | PPD - Auditorium | Unmet Hours (Heating) | Unmet Hours (Cooling) | UH Compliance | Peak Heating Load | Peak Cooling Load | Overheating Risk | EUI | Climate | [9 empty] | Climate | [9 empty] | Climate
1A | TMY2 | [5 empty] | 0 | 1 | 1 |  |  |  |  | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3 | [5 empty] | 2 | 1 | 3 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 34 | 07:30,23/Jan | 99 | 16:30,10/Sep | 91 |  | Heating plant sensible load | ASHRAE ZONING - FLOOR 1 | RL.htg | Load (Btu/h) | 1347474 | 12:00, January | 1347474 | 12:00, January | 1347474 |  | Cooling plant sensible load | ASHRAE ZONING - FLOOR 1 | RL.clg | Load (Btu/h) | 0 | 00:30, May | 836799 | 06:30, July | 242226
| TMY3WA | [5 empty] | 0 | 0 | 0 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 07:30,23/Jan | 60 | 14:30,10/Sep | 35 | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY7WA | [5 empty] | 0 | 1 | 1 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 60 | 00:30,01/Apr | 100 | 14:30,22/Mar | 95 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3817965 | 12:00, January | 3817965 | 12:00, January | 3817965 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 2088790 | 14:30, September | 706081
| TMY15WA | [5 empty] | 0 | 2 | 2 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 07:30,31/Mar | 67 | 15:30,22/Aug | 30 | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| XMY MAX | [5 empty] | 0 | 0 | 0 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 08:30,14/Jan | 59 | 07:30,05/Sep | 22 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3335691 | 12:00, January | 3335691 | 12:00, January | 3335691 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 33472 | 04:30, May | 2663299 | 13:30, September | 1158642
| XMYMIN | [5 empty] | 20 | 2 | 22 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 6 | 14:30,23/Jan | 62 | 03:30,17/Aug | 28 | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY2 | [5 empty] | 6 | 2 | 8 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 6 | 05:30,04/Jan | 99 | 16:30,10/Sep | 86 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4088501 | 12:00, January | 4088501 | 12:00, January | 4088501 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1750283 | 14:30, September | 596672
| TMY3 | [5 empty] | 1 | 2 | 3 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 06:30,29/Dec | 60 | 14:30,10/Sep | 32 | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3WA | [5 empty] | 1 | 8 | 9 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 18 | 07:30,03/Jan | 100 | 15:30,02/Apr | 93 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3619627 | 12:00, January | 3619627 | 12:00, January | 3619627 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 7055 | 04:30, May | 2283118 | 06:30, July | 948956
| TMY7WA | [5 empty] | 0 | 2 | 2 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 02:30,29/Jan | 67 | 17:30,17/Jul | 26 | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY15WA | [5 empty] | 0 | 3 | 3 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 08:30,12/Mar | 59 | 07:30,05/Sep | 19 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3224919 | 12:00, January | 3224919 | 12:00, January | 3224919 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1134247 | 16:30, September | 233197
| XMY MAX | [5 empty] | 0 | 14 | 14 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 13:30,02/Jan | 64 | 06:30,03/Jul | 25 | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| XMYMIN | [5 empty] | 23 | 2 | 25 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 6 | 05:30,04/Feb | 99 | 16:30,22/Sep | 83 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4186155 | 12:00, January | 4186155 | 12:00, January | 4186155 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1834987 | 14:30, September | 609641
2B | TMY2 | [5 empty] | 4 | 10 | 14 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 02:30,15/Dec | 56 | 14:30,09/Sep | 30 | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3 | [5 empty] | 0 | 19 | 19 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 31 | 05:30,04/Feb | 100 | 16:30,17/May | 91 |  | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 3979020 | 12:00, January | 3979020 | 12:00, January | 3979020 |  | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1620069 | 14:30, September | 492266
| TMY3WA | [5 empty] | 0 | 22 | 22 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 01:30,20/Mar | 66 | 12:30,02/Oct | 24 | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY7WA | [5 empty] | 0 | 17 | 17 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 08:30,14/Dec | 60 | 03:30,11/Sep | 18 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3717431 | 12:00, January | 3717431 | 12:00, January | 3717431 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1703772 | 14:30, September | 545748
| TMY15WA | [5 empty] | 2 | 13 | 15 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 20:30,20/Dec | 63 | 01:30,30/Oct | 24 | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| XMY MAX | [5 empty] | 0 | 25 | 25 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 6 | 01:30,13/Jan | 99 | 16:30,01/Sep | 83 |  | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 4783322 | 12:00, January | 4783322 | 12:00, January | 4783322 |  | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1715606 | 14:30, September | 547479+BF403
| XMYMIN | [5 empty] | 55 | 3 | 58 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 04:30,31/Jan | 52 | 16:30,09/Sep | 30 | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY2 | [5 empty] | 47 | 5 | 52 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 15 | 04:30,04/Jan | 100 | 15:30,19/May | 91 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4593129 | 12:00, January | 4593129 | 12:00, January | 4593129 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1623303 | 14:30, September | 435957
| TMY3 | [5 empty] | 29 | 7 | 36 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 01:30,20/Mar | 67 | 10:30,25/Jul | 24 | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3WA | [5 empty] | 0 | 6 | 6 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 08:30,09/Feb | 58 | 04:30,07/Oct | 18 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3909844 | 12:00, January | 3909844 | 12:00, January | 3909844 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1097704 | 16:30, September | 244993
| TMY7WA | [5 empty] | 4 | 3 | 7 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 16:30,03/Jan | 63 | 04:30,23/Aug | 24 | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY15WA | [5 empty] | 0 | 8 | 8 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 6 | 18:30,09/Jan | 99 | 16:30,07/Oct | 88 |  | Heating plant sensible load | 46 rooms | ROOMLOADS_TMY2.htg | Load (Btu/h) | 5063981 | 12:00, January | 5063981 | 12:00, January | 5063981 |  | Cooling plant sensible load | 46 rooms | ROOMLOADS_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1659937 | 14:30, September | 552584
| XMY MAX | [5 empty] | 0 | 12 | 12 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 01:30,04/Jan | 60 | 14:30,07/Oct | 33 | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| XMYMIN | [5 empty] | 188 | 2 | 190 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 31 | 07:30,09/Jan | 100 | 15:30,26/Mar | 94 |  | Heating plant sensible load | 46 rooms | ROOMLOAD_TMY2.htg | Load (Btu/h) | 5141729 | 12:00, January | 5141729 | 12:00, January | 5141729 |  | Cooling plant sensible load | 46 rooms | ROOMLOAD_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1535761 | 16:30, September | 413026
3B | TMY2 | [5 empty] | 15 | 13 | 28 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 03:30,03/Feb | 68 | 15:30,03/Jul | 28 | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3 | [5 empty] | 10 | 16 | 26 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 08:30,28/Dec | 59 | 04:30,25/Sep | 20 |  | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 5145132 | 12:00, January | 5145132 | 12:00, January | 5145132 |  | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1362498 | 14:30, September | 385377
| TMY3WA | [5 empty] | 8 | 15 | 23 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 17:30,04/Jan | 63 | 04:30,28/Oct | 27 | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY7WA | [5 empty] | 14 | 9 | 23 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 00:30,08/Mar | 99 | 16:30,08/Sep | 66 |  | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 5939305 | 12:00, January | 5939305 | 12:00, January | 5939305 |  | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1242278 | 16:30, May | 294945
| TMY15WA | [5 empty] | 10 | 16 | 26 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 07:30,06/Dec | 55 | 15:30,08/Sep | 23
| XMY MAX | [5 empty] | 0 | 23 | 23 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 6 | 16:30,24/Jan | 100 | 16:30,28/Apr | 81
| XMYMIN | [5 empty] | 115 | 0 | 115 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 03:30,08/Apr | 67 | 09:30,25/Jul | 19
3C | TMY2 | [5 empty] | 6 | 2 | 8 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 10:30,20/Nov | 56 | 00:30,26/Jul | 14
| TMY3 | [5 empty] | 2 | 2 | 4 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 17:30,11/Jan | 62 | 00:30,14/Aug | 18
| TMY3WA | [5 empty] | 0 | 8 | 8 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 77 | 07:30,15/Jan | 100 | 15:30,01/Sep | 93
| TMY7WA | [5 empty] | 2 | 2 | 4 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 20 | 08:30,16/Jan | 63 | 14:30,03/Sep | 38
| TMY15WA | [5 empty] | 0 | 5 | 5 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 85 | 01:30,18/Apr | 100 | 15:30,08/Mar | 96
| XMY MAX | [5 empty] | 0 | 22 | 22 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 6 | 11:30,20/Dec | 68 | 16:30,15/Aug | 33
| XMYMIN | [5 empty] | 36 | 0 | 36 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 11:30,04/Dec | 61 | 02:30,17/Sep | 24
4A | TMY2 | [5 empty] | 106 | 159 | 265 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 6 | 14:30,19/Dec | 63 | 18:30,18/Jul | 30
| TMY3 | [5 empty] | 96 | 133 | 229 |  |  |  |  | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3WA | [5 empty] | 11 | 196 | 207 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 19 | 05:30,18/Jan | 100 | 16:30,13/Sep | 85
| TMY7WA | [5 empty] | 25 | 122 | 147 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 07:30,22/Jan | 56 | 14:30,28/May | 27
| TMY15WA | [5 empty] | 26 | 192 | 218 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 23 | 05:30,27/Dec | 100 | 15:30,09/Apr | 87
| XMY MAX | [5 empty] | 1 | 173 | 174 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 11:30,27/Dec | 69 | 16:30,18/Jul | 21
| XMYMIN | [5 empty] | 371 | 109 | 480 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 11:30,27/Feb | 56 | 00:30,16/Aug | 15
4B | TMY2 | [5 empty] | 131 | 1219 | 1350 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 11:30,16/Jan | 63 | 05:30,21/Aug | 22
| TMY3 | [5 empty] | 112 | 1270 | 1382 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 8 | 05:30,21/Dec | 100 | 16:30,28/Sep | 88
| TMY3WA | [5 empty] | 59 | 1758 | 1817 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 08:30,19/Jan | 61 | 15:30,20/Sep | 29
| TMY7WA | [5 empty] | 118 | 1490 | 1608 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 8 | 06:30,20/Dec | 100 | 15:30,11/May | 90
| TMY15WA | [5 empty] | 122 | 1754 | 1876 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 05:30,21/Feb | 67 | 11:30,18/Jul | 23
| XMY MAX | [5 empty] | 14 | 2341 | 2355 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 11:30,07/Feb | 58 | 03:30,28/Sep | 16
| XMYMIN | [5 empty] | 539 | 484 | 1023 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 12:30,25/Dec | 63 | 05:30,07/Jul | 24
4C | TMY2 | [5 empty] | 46 | 118 | 164 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 18 | 05:30,15/Feb | 100 | 15:30,03/Aug | 82
| TMY3 | [5 empty] | 44 | 57 | 101 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 21:30,09/Jan | 51 | 14:30,21/Sep | 25
| TMY3WA | [5 empty] | 16 | 218 | 234 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 16 | 06:30,12/Feb | 100 | 16:30,11/May | 85
| TMY7WA | [5 empty] | 52 | 315 | 367 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 01:30,17/Mar | 67 | 10:30,25/Jul | 20
| TMY15WA | [5 empty] | 28 | 287 | 315 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 09:30,20/Mar | 53 | 21:30,01/Aug | 14
| XMY MAX | [5 empty] | 0 | 866 | 866 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 11:30,02/Jan | 64 | 07:30,04/Jul | 21
| XMYMIN | [5 empty] | 386 | 1 | 387 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 10 | 06:30,14/Jan | 100 | 16:30,16/Sep | 81
5A | TMY2 | [5 empty] | 208 | 89 | 297 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 08:30,23/Dec | 50 | 14:30,24/Sep | 25
| TMY3 | [5 empty] | 219 | 76 | 295 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 8 | 06:30,11/Jan | 100 | 14:30,18/May | 84
| TMY3WA | [5 empty] | 51 | 83 | 134 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 12:30,01/Feb | 67 | 10:30,17/Jul | 20
| TMY7WA | [5 empty] | 100 | 66 | 166 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 10:30,09/Jan | 51 | 04:30,05/Jul | 13
| TMY15WA | [5 empty] | 98 | 84 | 182 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 20:30,12/Jan | 64 | 07:30,11/Jul | 21
| XMY MAX | [5 empty] | 5 | 154 | 159 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 27 | 05:30,30/Dec | 100 | 16:30,13/Sep | 86
| XMYMIN | [5 empty] | 785 | 9 | 794 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 05:30,08/Mar | 56 | 14:30,14/Sep | 27
5B | TMY2 | [5 empty] | 265 | 1057 | 1322 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 23 | 05:30,27/Dec | 100 | 12:30,29/Apr | 88
| TMY3 | [5 empty] | 231 | 1077 | 1308 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 11:30,27/Dec | 68 | 08:30,06/Jun | 21
| TMY3WA | [5 empty] | 230 | 839 | 1069 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 13:30,10/Jan | 56 | 00:30,16/Aug | 15
| TMY7WA | [5 empty] | 295 | 867 | 1162 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 13:30,11/Dec | 66 | 07:30,06/Jun | 23
| TMY15WA | [5 empty] | 237 | 914 | 1151 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 7 | 17:30,18/Jan | 99 | 16:30,29/Jul | 63
| XMY MAX | [5 empty] | 73 | 1689 | 1762 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 04:30,19/Apr | 48 | 16:30,09/Sep | 21
| XMYMIN | [5 empty] | 1333 | 85 | 1418 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 7 | 17:30,13/Feb | 100 | 15:30,14/Jun | 69
5C | TMY2 | [5 empty] | 54 | 9 | 63 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 12:30,19/Jan | 67 | 18:30,18/Jul | 18
| TMY3 | [5 empty] | 56 | 9 | 65 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 12:30,30/Oct | 48 | 19:30,13/Jun | 12
| TMY3WA | [5 empty] | 10 | 115 | 125 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 18:30,16/Feb | 61 | 22:30,08/Aug | 16
| TMY7WA | [5 empty] | 33 | 32 | 65 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 72 | 00:30,18/Jan | 100 | 13:30,01/Sep | 94
| TMY15WA | [5 empty] | 16 | 29 | 45 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 10 | 00:30,18/Jan | 70 | 15:30,03/Sep | 35
| XMY MAX | [5 empty] | 0 | 356 | 356 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 70 | 00:30,18/Jan | 100 | 14:30,29/Mar | 95
| XMYMIN | [5 empty] | 365 | 0 | 365 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 6 | 10:30,15/Jan | 67 | 13:30,08/Aug | 28
6A | TMY2 | [5 empty] | 491 | 96 | 587 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 12:30,07/Feb | 59 | 03:30,28/Sep | 19
| TMY3 | [5 empty] | 404 | 150 | 554 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 6 | 09:30,25/Dec | 63 | 04:30,12/Jun | 27
| TMY3WA | [5 empty] | 106 | 195 | 301 |  |  |  |  | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY7WA | [5 empty] | 335 | 181 | 516 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,11/Mar | 58 | 02:30,23/Aug | 17
| TMY15WA | [5 empty] | 278 | 260 | 538 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 22:30,14/Dec | 51 | 13:30,02/Sep | 21
| XMY MAX | [5 empty] | 32 | 449 | 481 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,02/Dec | 59 | 14:30,28/Aug | 19
| XMYMIN | [5 empty] | 1079 | 92 | 1171 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 21:30,19/Jan | 62 | 13:30,01/Aug | 17
6B | TMY2 | [5 empty] | 426 | 686 | 1112 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 10:30,02/Jan | 53 | 21:30,15/Aug | 14
| TMY3 | [5 empty] | 344 | 645 | 989 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 08:30,26/Jan | 58 | 06:30,11/Jul | 16
| TMY3WA | [5 empty] | 214 | 947 | 1161 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 06:30,25/Nov | 55 | 14:30,25/Jul | 19
| TMY7WA | [5 empty] | 0 | 2153 | 2153 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 01:30,18/Feb | 52 | 13:30,09/Sep | 23
| TMY15WA | [5 empty] | 242 | 797 | 1039 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 06:30,12/Nov | 57 | 15:30,22/Aug | 20
| XMY MAX | [5 empty] | 97 | 1513 | 1610 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 02:30,22/Feb | 61 | 13:30,15/Aug | 19
| XMYMIN | [5 empty] | 1388 | 81 | 1469 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 16:30,18/Dec | 54 | 07:30,15/Aug | 15
7 | TMY2 | [5 empty] | 681 | 64 | 745 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 20:30,03/Dec | 57 | 05:30,15/Aug | 18
| TMY3 | [5 empty] | 613 | 65 | 678 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,11/Nov | 59 | 04:30,21/Jul | 20
| TMY3WA | [5 empty] | 198 | 152 | 350 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 09:30,22/Dec | 52 | 13:30,03/Sep | 23
| TMY7WA | [5 empty] | 407 | 145 | 552 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 06:30,28/Oct | 58 | 04:30,21/Jul | 22
| TMY15WA | [5 empty] | 290 | 103 | 393 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 00:30,23/Mar | 64 | 14:30,18/Jul | 20
| XMY MAX | [5 empty] | 52 | 281 | 333 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 08:30,08/Mar | 55 | 06:30,18/Jul | 16
| XMYMIN | [5 empty] | 1211 | 25 | 1236 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 10:30,17/Jan | 57 | 06:30,15/Aug | 18
8 | TMY2 | [5 empty] | 1316 | 97 | 1413 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 06:30,22/Apr | 54 | 09:30,03/Jul | 19
| TMY3 | [5 empty] | 1175 | 163 | 1338 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 01:30,14/Feb | 49 | 14:30,10/Sep | 22
| TMY3WA | [5 empty] | 671 | 450 | 1121 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 06:30,28/Jan | 59 | 13:30,12/Sep | 21
| TMY7WA | [5 empty] | 955 | 259 | 1214 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 20:30,11/Dec | 61 | 12:30,18/Jul | 19
| TMY15WA | [5 empty] | 873 | 445 | 1318 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 08:30,26/Nov | 55 | 19:30,11/Jul | 15
| XMY MAX | [5 empty] | 224 | 955 | 1179 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 19:30,20/Jan | 54 | 05:30,30/Aug | 17
| XMYMIN | [5 empty] | 1904 | 0 | 1904 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,15/Apr | 55 | 04:30,02/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 23:30,08/Dec | 51 | 14:30,06/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 06:30,02/Nov | 58 | 14:30,15/Aug | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 08:30,20/Nov | 60 | 18:30,01/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 16:30,31/Jan | 53 | 19:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 14:30,19/Dec | 56 | 04:30,26/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 08:30,20/Apr | 53 | 12:30,11/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 08:30,19/Apr | 46 | 14:30,06/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 06:30,08/Jun | 56 | 14:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 18:30,11/Jan | 59 | 15:30,24/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 12:30,03/Feb | 42 | 05:30,20/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 18:30,20/Jan | 54 | 05:30,20/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 06:30,10/Feb | 55 | 16:30,25/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 20:30,19/Dec | 55 | 14:30,08/Sep | 25
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,01/Feb | 58 | 12:30,04/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 02:30,26/Jan | 59 | 14:30,11/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 08:30,29/Dec | 56 | 05:30,02/Sep | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 08:30,17/Dec | 53 | 23:30,24/Aug | 19
[14 empty] | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 9 | 06:30,04/Jan | 99 | 16:30,12/Jul | 74
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 09:30,20/Feb | 54 | 14:30,06/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 10 | 06:30,04/Jan | 100 | 16:30,06/May | 78
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 14:30,07/Dec | 65 | 11:30,14/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 14:30,04/Dec | 52 | 01:30,26/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 12:30,12/Dec | 62 | 02:30,16/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 21 | 06:30,27/Feb | 99 | 15:30,26/Jul | 78
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 01:30,04/Mar | 51 | 14:30,19/May | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 20 | 05:30,25/Feb | 100 | 14:30,13/May | 82
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 12:30,19/Jan | 65 | 11:30,14/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 14:30,17/Jan | 47 | 20:30,27/Jun | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 13:30,27/Feb | 64 | 23:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 7 | 06:30,15/Feb | 99 | 13:30,09/Sep | 73
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 03:30,07/Mar | 49 | 14:30,09/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 7 | 16:30,14/Feb | 100 | 16:30,06/Jul | 77
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 11:30,28/Dec | 63 | 14:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 10:30,11/Jan | 44 | 20:30,13/Jun | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 17:30,26/Jan | 60 | 03:30,09/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 8 | 07:30,18/Jan | 98 | 17:30,02/Jul | 71
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 08:30,08/Nov | 46 | 14:30,14/May | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 8 | 05:30,19/Jan | 100 | 15:30,02/Jul | 76
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 04:30,28/Oct | 64 | 12:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 14:30,22/Dec | 44 | 21:30,03/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 20:30,29/Jan | 58 | 06:30,04/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 20 | 06:30,07/Feb | 99 | 16:30,12/Jul | 76
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 08:30,03/Mar | 51 | 15:30,07/Sep | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 16 | 05:30,02/Feb | 100 | 16:30,20/May | 80
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 12:30,19/Jan | 65 | 11:30,14/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 14:30,17/Jan | 52 | 01:30,26/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 15:30,24/Jan | 62 | 02:30,16/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 7 | 07:30,22/Feb | 97 | 16:30,09/Aug | 54
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 02:30,03/May | 44 | 16:30,10/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 8 | 17:30,07/Mar | 100 | 16:30,10/Sep | 60
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 14:30,29/Oct | 57 | 16:30,29/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 13:30,03/Feb | 40 | 06:30,24/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 13:30,18/Jan | 49 | 22:30,11/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 46 | 05:30,27/Dec | 100 | 15:30,30/Jun | 88
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 01:30,25/Jan | 55 | 17:30,07/Sep | 29
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 42 | 07:30,07/Feb | 100 | 16:30,29/Apr | 90
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 08:30,03/Jan | 64 | 13:30,08/Aug | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 14:30,25/Dec | 53 | 01:30,26/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 08:30,08/Feb | 61 | 01:30,30/Aug | 22
[14 empty] | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 07:30,22/Mar | 51 | 14:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 01:30,13/Mar | 49 | 13:30,17/Sep | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 06:30,22/Oct | 53 | 11:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 04:30,18/Apr | 56 | 09:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 09:30,13/Nov | 60 | 05:30,20/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 15:30,27/Dec | 55 | 07:30,11/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,28/Oct | 52 | 08:30,22/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 00:30,25/Feb | 49 | 13:30,17/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,18/Mar | 56 | 13:30,07/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 08:30,30/Mar | 57 | 14:30,22/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 09:30,13/Nov | 61 | 05:30,06/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 15:30,07/Jan | 55 | 06:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,02/Apr | 53 | 01:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 09:30,29/Mar | 51 | 14:30,02/Sep | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,15/Apr | 55 | 12:30,07/Aug | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 20:30,03/Feb | 59 | 12:30,07/Aug | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 12:30,06/Nov | 55 | 06:30,13/Dec | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 14:30,15/Feb | 54 | 06:30,07/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 06:30,06/Apr | 51 | 14:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 01:30,26/Mar | 52 | 06:30,11/Jan | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 06:30,02/Apr | 55 | 13:30,07/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 10:30,08/Feb | 67 | 06:30,11/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 09:30,25/Feb | 69 | 06:30,11/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 17:30,12/Mar | 54 | 06:30,07/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,05/Apr | 53 | 00:30,02/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 08:30,15/Apr | 50 | 14:30,03/Sep | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,18/Mar | 53 | 11:30,11/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 00:30,16/Mar | 56 | 09:30,11/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 09:30,13/Nov | 61 | 05:30,06/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 15:30,23/Dec | 55 | 07:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 06:30,20/May | 45 | 14:30,31/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 01:30,12/May | 66 | 05:30,18/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 06:30,31/Aug | 52 | 14:30,22/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 08:30,29/May | 79 | 07:30,17/Jan | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 15:30,08/May | 80 | 05:30,18/Jan | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 14:30,02/Dec | 58 | 15:30,17/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 06:30,12/Mar | 51 | 13:30,05/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 01:30,23/Jan | 54 | 14:30,03/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,10/Nov | 56 | 12:30,05/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 00:30,01/Dec | 59 | 14:30,05/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 11:30,20/Nov | 52 | 04:30,24/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 16:30,27/Dec | 53 | 01:30,27/Jul | 17
[14 empty] | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 22 | 05:30,11/Jan | 88 | 14:30,14/Oct | 56
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 02:30,01/Sep | 31 | 06:30,11/Jan | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 23 | 07:30,10/Jan | 98 | 14:30,14/Oct | 62
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 09:30,12/Jan | 26 | 03:30,11/Jan | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 13:30,21/Mar | 27 | 07:30,10/Jan | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 20:30,11/Jan | 25 | 10:30,14/Oct | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 25 | 05:30,09/Feb | 92 | 14:30,05/Oct | 63
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 23:30,30/Jul | 27 | 14:30,05/Oct | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 23 | 05:30,09/Feb | 98 | 14:30,23/Sep | 68
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 14:30,30/Mar | 31 | 15:30,03/Oct | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 09:30,25/Dec | 22 | 05:30,08/Feb | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 19:30,30/Dec | 29 | 06:30,25/Sep | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 24 | 05:30,11/Jan | 89 | 14:30,24/Sep | 57
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 23:30,22/May | 31 | 06:30,11/Jan | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 23 | 07:30,26/Dec | 98 | 15:30,15/Sep | 63
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 04:30,27/Sep | 25 | 05:30,27/Dec | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 09:30,18/Dec | 26 | 05:30,27/Dec | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 12:30,25/Dec | 23 | 10:30,12/May | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 22 | 05:30,26/Dec | 92 | 14:30,30/Sep | 54
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 00:30,13/Sep | 34 | 07:30,26/Dec | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 21 | 07:30,02/Jan | 98 | 16:30,28/Sep | 60
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 08:30,23/Mar | 36 | 14:30,03/Jul | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 13:30,20/Mar | 29 | 05:30,26/Dec | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 09:30,10/Apr | 29 | 04:30,30/Sep | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 28 | 07:30,25/Dec | 92 | 14:30,20/Sep | 58
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 01:30,10/Oct | 27 | 14:30,20/Sep | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 28 | 05:30,20/Jan | 98 | 14:30,17/Sep | 64
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 11:30,10/Mar | 41 | 14:30,19/Sep | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 15:30,17/Jan | 18 | 17:30,31/May | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 08:30,06/Dec | 29 | 19:30,19/Sep | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 20 | 05:30,13/Jan | 79 | 14:30,10/Sep | 44
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 02:30,11/Sep | 37 | 04:30,13/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 20 | 05:30,13/Jan | 94 | 15:30,10/Sep | 51
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 14:30,15/Mar | 28 | 03:30,06/Dec | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 13:30,12/Jun | 30 | 02:30,06/Dec | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 17:30,27/Jan | 19 | 13:30,09/Sep | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 39 | 23:30,03/Jan | 93 | 14:30,30/Sep | 69
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 21:30,04/Dec | 30 | 14:30,13/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 38 | 00:30,04/Jan | 99 | 14:30,13/Sep | 74
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 07:30,18/Mar | 47 | 15:30,29/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 15:30,14/Feb | 22 | 17:30,26/Oct | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 08:30,20/Jan | 36 | 19:30,29/Aug | 12
[14 empty] | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 07:30,27/Oct | 60 | 08:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 00:30,17/Nov | 79 | 14:30,23/Jul | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,19/Oct | 58 | 09:30,25/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 09:30,12/Jan | 63 | 12:30,25/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 14:30,05/Dec | 45 | 07:30,24/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 20:30,04/Mar | 60 | 07:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,04/May | 60 | 08:30,25/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 08:30,02/Apr | 79 | 14:30,23/Jul | 25
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,31/Mar | 58 | 09:30,25/Jul | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 15:30,11/Nov | 63 | 12:30,25/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 10:30,09/Jan | 47 | 17:30,30/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 20:30,28/Jan | 60 | 07:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,22/Apr | 55 | 12:30,05/Sep | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 00:30,02/May | 73 | 16:30,06/Sep | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,20/Oct | 57 | 18:30,05/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 08:30,10/Apr | 64 | 13:30,05/Sep | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 08:30,02/Nov | 44 | 20:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 18:30,04/Feb | 56 | 07:30,11/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,05/May | 55 | 10:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 23:30,18/Oct | 68 | 16:30,09/Aug | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,30/Apr | 59 | 09:30,25/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 20:30,14/Jan | 68 | 10:30,25/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 10:30,09/Jan | 45 | 05:30,18/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 20:30,22/Jan | 58 | 22:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,05/Nov | 60 | 08:30,25/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 06:30,02/Nov | 79 | 14:30,23/Jul | 25
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,17/Mar | 58 | 09:30,25/Jul | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 20:30,12/Feb | 63 | 12:30,25/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 12:30,28/Mar | 45 | 07:30,24/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 15:30,18/Apr | 60 | 07:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,30/Sep | 39 | 07:30,24/Jan | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 01:30,26/May | 42 | 16:30,08/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,30/Sep | 52 | 18:30,01/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 08:30,12/Jun | 46 | 18:30,01/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 11:30,14/Jan | 45 | 05:30,11/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 13:30,06/Dec | 40 | 19:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,12/Feb | 58 | 04:30,08/Aug | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 08:30,30/Jan | 84 | 18:30,31/May | 34
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,31/Mar | 61 | 14:30,31/Jul | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 07:30,29/Mar | 65 | 13:30,01/Aug | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 15:30,26/Dec | 53 | 00:30,05/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 13:30,14/Feb | 60 | 05:30,08/Aug | 20
[14 empty] | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,17/May | 41 | 16:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 21:30,14/Apr | 77 | 14:30,20/Jul | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,22/Oct | 50 | 14:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 14:30,12/Feb | 54 | 13:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 14:30,27/Jan | 62 | 18:30,02/Sep | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 12:30,14/Mar | 41 | 19:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,25/Mar | 41 | 14:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 01:30,04/Nov | 75 | 14:30,08/Sep | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 06:30,12/May | 54 | 12:30,11/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 10:30,11/Apr | 56 | 13:30,11/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 12:30,14/Mar | 63 | 18:30,02/Sep | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 16:30,19/Jan | 39 | 07:30,01/Aug | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,27/Apr | 44 | 15:30,25/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 21:30,18/Apr | 73 | 14:30,29/Jun | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,11/May | 52 | 15:30,21/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 11:30,19/Mar | 53 | 10:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 16:30,11/Jan | 63 | 18:30,20/May | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 20:30,01/Dec | 43 | 07:30,04/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 06:30,20/Apr | 46 | 21:30,01/Aug | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 09:30,18/Apr | 68 | 15:30,03/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,12/Oct | 53 | 14:30,01/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 12:30,18/Mar | 54 | 15:30,01/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 14:30,10/Apr | 64 | 19:30,20/May | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 18:30,27/Jan | 49 | 22:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,27/Apr | 41 | 16:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 00:30,10/Apr | 77 | 14:30,20/Jul | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 06:30,12/May | 51 | 14:30,28/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 11:30,03/Mar | 54 | 13:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 15:30,07/Nov | 61 | 18:30,24/Sep | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 14:30,23/Jan | 41 | 19:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 06:30,16/Jun | 41 | 04:30,03/Feb | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 00:30,22/May | 67 | 06:30,03/Feb | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,04/Jun | 45 | 16:30,31/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 19:30,22/Feb | 47 | 03:30,03/Feb | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 16:30,23/Mar | 57 | 19:30,31/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 21:30,08/Oct | 40 | 20:30,02/Feb | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,25/Mar | 43 | 18:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 22:30,09/Nov | 80 | 18:30,31/May | 27
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,23/Apr | 52 | 13:30,29/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 11:30,02/Feb | 53 | 14:30,17/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 14:30,06/Mar | 68 | 18:30,31/May | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 19:30,15/Feb | 42 | 19:30,08/Aug | 13
[14 empty] | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,10/Jun | 40 | 15:30,01/Aug | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 21:30,19/Jun | 64 | 16:30,10/Sep | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,14/Oct | 53 | 14:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 15:30,12/Jan | 54 | 14:30,01/Aug | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 09:30,18/Jan | 50 | 17:30,07/May | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 12:30,24/Apr | 38 | 19:30,01/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,04/Oct | 32 | 15:30,15/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 14:30,06/Jun | 59 | 16:30,15/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 06:30,13/Sep | 48 | 14:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 08:30,09/Nov | 43 | 16:30,14/Aug | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 09:30,21/Feb | 51 | 17:30,06/Sep | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 13:30,28/Feb | 29 | 18:30,15/Aug | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 07:30,15/Oct | 34 | 20:30,09/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 01:30,28/Oct | 52 | 16:30,10/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,06/Oct | 49 | 18:30,21/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 02:30,08/Oct | 41 | 16:30,05/Jun | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 13:30,23/May | 48 | 19:30,05/Apr | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 16:30,06/Dec | 35 | 19:30,08/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,09/Apr | 33 | 20:30,09/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 09:30,12/Jun | 52 | 17:30,10/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,04/Oct | 45 | 18:30,09/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 15:30,11/Jan | 42 | 05:30,31/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 09:30,29/Jan | 56 | 19:30,17/May | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 15:30,10/Apr | 35 | 20:30,15/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,10/Jun | 40 | 15:30,01/Aug | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 21:30,19/Jun | 64 | 16:30,10/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,22/Apr | 53 | 14:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 12:30,08/Jan | 54 | 14:30,01/Aug | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 10:30,02/Dec | 49 | 17:30,07/Sep | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 13:30,13/Mar | 38 | 19:30,01/Aug | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,02/Jul | 35 | 07:30,07/Feb | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 23:30,10/Sep | 40 | 06:30,08/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,15/Sep | 36 | 04:30,08/Dec | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 09:30,27/May | 44 | 02:30,01/Nov | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 12:30,05/Feb | 36 | 07:30,07/Feb | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 15:30,24/Nov | 36 | 07:30,07/Feb | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,16/Apr | 41 | 13:30,15/Aug | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 11:30,17/Apr | 70 | 17:30,02/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,15/Oct | 55 | 14:30,15/Aug | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 09:30,30/Nov | 53 | 16:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 14:30,20/Feb | 59 | 17:30,06/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 14:30,27/Feb | 46 | 19:30,15/Aug | 12
[14 empty] | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY7_WA.aps | Percentage (%) | 5 | 07:30,21/Oct | 49 | 11:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY7_WA.aps | Percentage (%) | 5 | 08:30,11/May | 69 | 16:30,09/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY7_WA.aps | Percentage (%) | 5 | 07:30,27/Oct | 56 | 13:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY7_WA.aps | Percentage (%) | 5 | 07:30,07/Oct | 63 | 11:30,24/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY7_WA.aps | Percentage (%) | 5 | 08:30,09/Apr | 39 | 07:30,24/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY7_WA.aps | Percentage (%) | 5 | 17:30,31/Dec | 52 | 01:30,19/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY3_WA.aps | Percentage (%) | 5 | 07:30,19/Nov | 51 | 18:30,15/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY3_WA.aps | Percentage (%) | 5 | 08:30,16/Nov | 69 | 16:30,13/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY3_WA.aps | Percentage (%) | 5 | 07:30,19/Nov | 55 | 16:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY3_WA.aps | Percentage (%) | 5 | 08:30,25/Nov | 61 | 12:30,29/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY3_WA.aps | Percentage (%) | 5 | 13:30,09/May | 44 | 18:30,23/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY3_WA.aps | Percentage (%) | 5 | 16:30,05/Mar | 51 | 23:30,14/Aug | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY3.aps | Percentage (%) | 5 | 15:30,10/Nov | 53 | 01:30,19/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY3.aps | Percentage (%) | 5 | 01:30,04/May | 69 | 14:30,19/Jul | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY3.aps | Percentage (%) | 5 | 06:30,20/Apr | 57 | 15:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY3.aps | Percentage (%) | 5 | 23:30,05/Oct | 63 | 11:30,17/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY3.aps | Percentage (%) | 5 | 12:30,23/Oct | 47 | 05:30,07/Feb | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY3.aps | Percentage (%) | 5 | 18:30,18/Mar | 59 | 20:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY2.aps | Percentage (%) | 5 | 07:30,01/Oct | 47 | 18:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY2.aps | Percentage (%) | 5 | 01:30,04/May | 60 | 14:30,19/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY2.aps | Percentage (%) | 5 | 07:30,28/Oct | 53 | 19:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY2.aps | Percentage (%) | 5 | 18:30,24/Mar | 59 | 13:30,03/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY2.aps | Percentage (%) | 5 | 11:30,08/Mar | 44 | 18:30,26/May | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY2.aps | Percentage (%) | 5 | 17:30,10/Nov | 50 | 19:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY15_WA.aps | Percentage (%) | 5 | 07:30,19/Nov | 49 | 11:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY15_WA.aps | Percentage (%) | 5 | 08:30,16/Nov | 69 | 16:30,13/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY15_WA.aps | Percentage (%) | 5 | 07:30,30/Sep | 56 | 13:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY15_WA.aps | Percentage (%) | 5 | 08:30,25/Nov | 63 | 11:30,24/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY15_WA.aps | Percentage (%) | 5 | 14:30,03/Apr | 44 | 18:30,23/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY15_WA.aps | Percentage (%) | 5 | 12:30,06/Nov | 52 | 01:30,19/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_MIN_WA.aps | Percentage (%) | 5 | 07:30,16/Sep | 42 | 04:30,31/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_MIN_WA.aps | Percentage (%) | 5 | 20:30,18/Sep | 43 | 07:30,31/Jan | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_MIN_WA.aps | Percentage (%) | 5 | 07:30,16/Sep | 41 | 05:30,31/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_MIN_WA.aps | Percentage (%) | 5 | 21:30,02/Jun | 46 | 03:30,31/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_MIN_WA.aps | Percentage (%) | 5 | 21:30,01/Nov | 47 | 00:30,31/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_MIN_WA.aps | Percentage (%) | 5 | 18:30,02/Apr | 40 | 01:30,18/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_MAX_WA.aps | Percentage (%) | 5 | 07:30,12/Nov | 58 | 02:30,19/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_MAX_WA.aps | Percentage (%) | 5 | 09:30,11/Mar | 79 | 17:30,02/Sep | 26
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_MAX_WA.aps | Percentage (%) | 5 | 07:30,28/Apr | 58 | 14:30,07/Aug | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_MAX_WA.aps | Percentage (%) | 5 | 12:30,04/Feb | 62 | 13:30,22/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_MAX_WA.aps | Percentage (%) | 5 | 08:30,11/Feb | 48 | 01:30,26/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_MAX_WA.aps | Percentage (%) | 5 | 17:30,15/Jan | 59 | 03:30,19/Jul | 17
[14 empty] | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,21/Jun | 41 | 01:30,07/Feb | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,19/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 06:30,11/Aug | 50 | 14:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 16:30,25/Jan | 51 | 15:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 12:30,04/Mar | 52 | 17:30,03/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 11:30,10/Apr | 39 | 07:30,07/Feb | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 06:30,07/Jun | 38 | 04:30,24/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,19/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 06:30,11/Aug | 50 | 14:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 18:30,08/Jan | 51 | 15:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 12:30,13/Jan | 52 | 17:30,03/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 12:30,21/Mar | 35 | 05:30,23/Dec | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 22:30,10/Jun | 42 | 04:30,13/Dec | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 23:30,05/Oct | 69 | 16:30,09/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,14/Sep | 47 | 13:30,01/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 00:30,11/May | 49 | 16:30,27/Jun | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 10:30,13/Nov | 63 | 19:30,28/May | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 17:30,27/Jan | 39 | 21:30,17/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,08/Jun | 42 | 04:30,13/Dec | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 01:30,10/Jun | 70 | 17:30,02/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,04/Oct | 48 | 14:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 22:30,29/May | 50 | 16:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 11:30,01/Mar | 65 | 18:30,02/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 15:30,13/Nov | 42 | 19:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,03/Jun | 38 | 04:30,24/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,03/Sep | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 06:30,23/Aug | 46 | 14:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 18:30,08/Jan | 49 | 14:30,25/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 11:30,31/Dec | 54 | 18:30,28/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 12:30,21/Mar | 38 | 04:30,24/Dec | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,12/Jul | 45 | 04:30,06/Dec | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 22:30,12/Aug | 51 | 05:30,02/Feb | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,20/Jul | 44 | 04:30,02/Feb | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 16:30,05/Mar | 48 | 03:30,06/Dec | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 11:30,17/Nov | 48 | 04:30,06/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 20:30,14/Jun | 41 | 05:30,06/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 06:30,05/May | 38 | 15:30,25/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 09:30,20/Apr | 64 | 15:30,03/Sep | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,23/Sep | 48 | 14:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 13:30,07/Dec | 50 | 12:30,25/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 11:30,03/Apr | 63 | 18:30,31/May | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 17:30,02/Feb | 35 | 18:30,25/Jul | 11
[14 empty] | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 07:30,07/Oct | 30 | 04:30,04/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 23:30,24/Jun | 36 | 16:30,15/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,04/Oct | 36 | 15:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 10:30,12/Apr | 40 | 00:30,01/Feb | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 07:30,24/May | 36 | 17:30,15/Sep | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 17:30,06/Dec | 25 | 10:30,07/Sep | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,17/May | 28 | 04:30,27/Dec | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 22:30,08/May | 48 | 18:30,28/May | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,28/Oct | 46 | 15:30,25/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 12:30,15/Jan | 32 | 16:30,25/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 14:30,20/Mar | 61 | 18:30,28/May | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 17:30,07/Dec | 30 | 10:30,09/Sep | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 06:30,16/Jun | 45 | 12:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 10:30,09/Oct | 62 | 17:30,20/Jul | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,30/Apr | 53 | 15:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 14:30,11/Oct | 63 | 14:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 12:30,26/Sep | 49 | 01:30,08/Mar | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 17:30,16/Nov | 51 | 04:30,21/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,29/Apr | 30 | 15:30,11/Jul | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 23:30,18/Jun | 36 | 15:30,11/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,29/Sep | 52 | 14:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 11:30,01/Apr | 50 | 14:30,11/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 07:30,24/May | 31 | 23:30,31/Oct | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 16:30,04/Nov | 32 | 19:30,11/Jul | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,27/Aug | 39 | 03:30,20/Dec | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 23:30,03/Sep | 46 | 05:30,20/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,27/Aug | 38 | 03:30,04/Jan | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 12:30,15/Apr | 43 | 16:30,07/Feb | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 15:30,15/Jan | 46 | 05:30,20/Dec | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 19:30,01/Apr | 38 | 02:30,20/Dec | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,29/Apr | 31 | 15:30,11/Jul | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 15:30,17/Oct | 56 | 19:30,28/May | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,08/Apr | 53 | 14:30,11/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 21:30,12/Mar | 52 | 18:30,11/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 13:30,24/Oct | 64 | 19:30,28/May | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 13:30,24/Oct | 38 | 19:30,11/Jul | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | doeCWEC.aps | Percentage (%) | 5 | 07:30,14/May | 34 | 04:30,22/Nov | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | doeCWEC.aps | Percentage (%) | 5 | 01:30,16/Oct | 33 | 04:30,22/Nov | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | doeCWEC.aps | Percentage (%) | 5 | 07:30,22/Oct | 42 | 16:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | doeCWEC.aps | Percentage (%) | 5 | 07:30,08/Jul | 43 | 03:30,22/Nov | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | doeCWEC.aps | Percentage (%) | 5 | 15:30,02/May | 34 | 03:30,22/Nov | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | doeCWEC.aps | Percentage (%) | 5 | 19:30,29/Oct | 26 | 04:30,22/Nov | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | CWEC.aps | Percentage (%) | 5 | 07:30,14/May | 33 | 03:30,22/Nov | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | CWEC.aps | Percentage (%) | 5 | 01:30,16/Oct | 33 | 04:30,22/Nov | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | CWEC.aps | Percentage (%) | 5 | 07:30,22/Oct | 41 | 15:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | CWEC.aps | Percentage (%) | 5 | 21:30,10/Mar | 43 | 03:30,22/Nov | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | CWEC.aps | Percentage (%) | 5 | 15:30,02/May | 34 | 03:30,22/Nov | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | CWEC.aps | Percentage (%) | 5 | 16:30,24/Dec | 26 | 04:30,22/Nov | 9
[14 empty] | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,13/May | 45 | 13:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 22:30,04/Oct | 67 | 17:30,09/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,13/Oct | 58 | 13:30,08/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 01:30,03/Sep | 63 | 17:30,04/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 09:30,22/Mar | 48 | 05:30,24/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 19:30,03/Nov | 48 | 19:30,04/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,21/Apr | 52 | 11:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 15:30,07/Nov | 68 | 18:30,18/Jul | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,16/Apr | 59 | 11:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 19:30,23/Feb | 65 | 12:30,17/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 13:30,13/Mar | 49 | 17:30,21/May | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 15:30,24/Oct | 59 | 19:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,07/May | 50 | 12:30,04/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 01:30,05/May | 65 | 17:30,19/Jul | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,19/Apr | 56 | 15:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 20:30,01/Dec | 64 | 14:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 12:30,20/Dec | 50 | 04:30,31/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 17:30,01/Mar | 57 | 20:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,10/May | 47 | 12:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 15:30,03/Oct | 64 | 18:30,28/May | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,26/Mar | 52 | 17:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 16:30,16/Mar | 61 | 16:30,17/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 15:30,25/Sep | 48 | 07:30,10/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 17:30,19/Nov | 49 | 07:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,13/May | 50 | 17:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 04:30,06/Oct | 66 | 18:30,04/Jul | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,13/Oct | 58 | 15:30,03/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 21:30,08/Apr | 61 | 11:30,08/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 08:30,24/Mar | 42 | 19:30,04/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 13:30,02/Oct | 57 | 19:30,04/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,25/Jun | 44 | 04:30,01/Feb | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 08:30,28/Jun | 45 | 06:30,21/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,25/Jun | 44 | 04:30,21/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 12:30,17/May | 51 | 05:30,01/Feb | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 11:30,15/Mar | 49 | 06:30,03/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 15:30,26/Sep | 40 | 04:30,31/Jan | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,08/Apr | 58 | 19:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 09:30,26/Nov | 85 | 19:30,18/Jul | 29
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,15/Oct | 60 | 17:30,18/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 14:30,08/Jan | 65 | 13:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 10:30,03/Mar | 63 | 05:30,19/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 13:30,20/Nov | 60 | 18:30,18/Jul | 17
[14 empty] | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 10 | 07:30,23/Jul | 63 | 04:30,10/May | 36
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 32 | 07:30,19/Jan | 93 | 19:30,07/Apr | 65
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 8 | 07:30,19/Jan | 60 | 03:30,05/Apr | 37
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 11 | 21:30,24/Dec | 78 | 18:30,24/May | 37
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 9 | 08:30,19/Jan | 54 | 05:30,06/Apr | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 15 | 07:30,28/Jul | 84 | 13:30,03/Sep | 38
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,02/Jun | 38 | 17:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 23:30,07/Oct | 63 | 16:30,22/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,27/May | 53 | 15:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 03:30,11/Jul | 52 | 16:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 13:30,15/Mar | 59 | 18:30,01/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 16:30,22/Mar | 39 | 19:30,18/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 07:30,20/May | 40 | 01:30,27/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 09:30,15/May | 55 | 17:30,15/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,22/Jun | 50 | 15:30,08/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 20:30,03/Dec | 47 | 16:30,08/Aug | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 14:30,22/Jan | 58 | 18:30,25/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 16:30,08/Mar | 39 | 01:30,18/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,11/Jun | 43 | 05:30,12/Dec | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 01:30,18/Jun | 57 | 15:30,30/Jun | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,01/Sep | 48 | 15:30,26/Jun | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 11:30,20/Apr | 50 | 06:30,12/Dec | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 08:30,05/Oct | 54 | 17:30,02/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 18:30,30/Dec | 40 | 05:30,13/Dec | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,17/Jun | 35 | 04:30,30/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 08:30,23/Jun | 57 | 14:30,29/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,24/Sep | 46 | 14:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 18:30,12/Jan | 50 | 14:30,24/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 09:30,24/May | 58 | 18:30,02/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 12:30,16/Oct | 37 | 05:30,30/Dec | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,11/Aug | 43 | 04:30,06/Dec | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 22:30,11/Aug | 48 | 06:30,17/Feb | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,11/Aug | 45 | 04:30,17/Feb | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 17:30,04/Mar | 50 | 04:30,20/Dec | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 17:30,08/Jun | 49 | 02:30,05/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 10:30,04/Sep | 42 | 05:30,18/Feb | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 06:30,12/May | 40 | 13:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 22:30,28/Oct | 68 | 14:30,16/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,21/Sep | 50 | 12:30,01/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 19:30,09/Feb | 49 | 13:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 13:30,13/Mar | 65 | 18:30,03/Sep | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 11:30,06/Nov | 41 | 19:30,01/Aug | 11
[14 empty] | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 07:30,22/Sep | 42 | 13:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 23:30,06/Oct | 55 | 14:30,07/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,21/Sep | 51 | 15:30,04/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 10:30,20/Oct | 59 | 16:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 11:30,19/Jan | 46 | 07:30,03/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 18:30,02/Nov | 46 | 07:30,04/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 06:30,25/May | 47 | 16:30,04/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 22:30,13/May | 58 | 15:30,31/May | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,24/Mar | 57 | 16:30,04/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 13:30,07/Apr | 60 | 11:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 11:30,25/Jan | 49 | 17:30,05/May | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 17:30,22/Nov | 48 | 07:30,04/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 07:30,12/May | 42 | 03:30,20/Dec | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 23:30,29/Sep | 44 | 16:30,26/May | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,10/Sep | 54 | 14:30,17/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 20:30,22/Mar | 57 | 16:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 12:30,26/Feb | 49 | 00:30,20/Dec | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 18:30,13/Apr | 45 | 18:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,24/Jun | 43 | 04:30,01/Feb | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 21:30,05/Jun | 47 | 16:30,08/Jul | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,23/Jun | 50 | 16:30,11/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 09:30,12/May | 51 | 05:30,08/Feb | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 14:30,12/Feb | 49 | 01:30,01/Feb | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 19:30,02/Nov | 43 | 20:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,15/Oct | 51 | 10:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 23:30,15/Apr | 60 | 12:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,30/Sep | 57 | 12:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 20:30,19/Feb | 65 | 12:30,17/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 11:30,01/Mar | 37 | 05:30,25/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 12:30,13/Nov | 53 | 07:30,18/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,20/Aug | 45 | 18:30,17/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 09:30,12/Aug | 47 | 19:30,17/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,27/Jul | 46 | 07:30,17/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 19:30,26/Mar | 51 | 22:30,17/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 16:30,23/Mar | 49 | 07:30,17/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 16:30,07/Oct | 43 | 22:30,17/Jan | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,26/Apr | 56 | 09:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 23:30,11/Apr | 73 | 13:30,18/Jul | 24
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,15/Oct | 59 | 13:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 13:30,05/Apr | 64 | 10:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 10:30,13/Mar | 50 | 17:30,29/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 15:30,03/Apr | 56 | 19:30,18/Jul | 15
[14 empty] | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,20/Aug | 44 | 03:30,28/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 00:30,04/Sep | 45 | 04:30,28/Jan | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,26/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 23:30,19/May | 48 | 05:30,19/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 10:30,13/Jun | 55 | 19:30,26/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 17:30,02/Apr | 43 | 20:30,27/Jan | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 06:30,02/Sep | 42 | 00:30,06/Dec | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 00:30,11/Sep | 54 | 16:30,28/Jun | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,27/Aug | 51 | 15:30,19/Jun | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 10:30,28/Apr | 50 | 15:30,19/Jun | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 14:30,05/Mar | 52 | 18:30,12/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 17:30,08/Apr | 41 | 21:30,27/Jun | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 07:30,19/May | 44 | 04:30,01/Mar | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 22:30,19/Aug | 45 | 04:30,01/Mar | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,12/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 16:30,11/Mar | 52 | 04:30,01/Mar | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 10:30,21/Aug | 50 | 20:30,05/Dec | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 17:30,29/Sep | 41 | 02:30,01/Mar | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,03/Jun | 49 | 04:30,04/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 09:30,13/Jun | 50 | 05:30,04/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,27/Aug | 49 | 01:30,04/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 13:30,18/May | 55 | 01:30,04/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 15:30,19/Mar | 52 | 04:30,03/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 20:30,22/Apr | 47 | 05:30,04/Jan | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,21/May | 40 | 06:30,21/Feb | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 09:30,23/Sep | 54 | 16:30,28/Jun | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,22/Sep | 51 | 15:30,19/Jun | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 18:30,12/Feb | 50 | 15:30,19/Jun | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 10:30,28/Oct | 47 | 04:30,21/Feb | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 17:30,07/Apr | 41 | 21:30,27/Jun | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,02/Jul | 49 | 03:30,18/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 11:30,15/Jul | 51 | 06:30,11/Jan | 26
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,16/Jul | 50 | 04:30,11/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 13:30,03/Sep | 56 | 05:30,11/Jan | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 12:30,12/Oct | 52 | 04:30,01/Feb | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 17:30,31/Aug | 47 | 05:30,11/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,24/Sep | 40 | 20:30,27/Jun | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 01:30,02/Oct | 68 | 18:30,28/May | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,31/Aug | 51 | 15:30,20/Jun | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 10:30,08/Oct | 50 | 16:30,03/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 10:30,12/Sep | 66 | 18:30,25/May | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 14:30,09/Oct | 45 | 22:30,27/Jun | 12

## pslpd Summary of Results
| Building Area (ft2): | 211975
1A - Miami | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 45198 | 1410542 | 995949 | 63280 | 804355 | 409348 | 0 | 90035 | 148866 | 27347 | 609959 | 3994920 | 18.8462 | max EUI | max EUI
| TMY3 DOE | 47631 | 1497298 | 995949 | 64293 | 804355 | 421762 | 0 | 95572 | 148866 | 27347 | 609959 | 4103073 | 19.3564 | 22.9867 | 21.5892
| TMY3 WA | 15226 | 1905895 | 995949 | 65108 | 804355 | 491970 | 0 | 121653 | 148866 | 27347 | 609959 | 4576369 | 21.5892 | min EUI | min EUI
| TMY7 WA | 30171 | 1658652 | 995949 | 65577 | 804355 | 450554 | 0 | 105871 | 148866 | 27347 | 609959 | 4287342 | 20.2257 | 17.1838 | 18.8462
| TMY15 WA | 26303 | 1761946 | 995949 | 65331 | 804355 | 473702 | 0 | 112465 | 148866 | 27347 | 609959 | 4416264 | 20.8339 | variance | variance
| XMY Min WA | 211651 | 979896 | 995949 | 66079 | 804355 | 345846 | 0 | 62547 | 148866 | 27347 | 609959 | 3642536 | 17.1838 | 29.98% | 14.17%
| XMY Max WA | 11310 | 2150903 | 995949 | 64192 | 804355 | 532390 | 0 | 137292 | 148866 | 27347 | 609959 | 4872604 | 22.9867
2A - Houston | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 623071 | 964210 | 690919 | 63933 | 482612 | 348365 | 0 | 61545 | 148866 | 27347 | 609959 | 3410868 | 16.0909 | max EUI | max EUI
| TMY3 DOE | 561126 | 1007777 | 690919 | 64622 | 482612 | 357821 | 0 | 64326 | 148866 | 27347 | 609959 | 3405416 | 16.0652 | 19.375 | 16.7358
| TMY3 WA | 301606 | 1349216 | 690919 | 66959 | 482612 | 393928 | 0 | 86120 | 148866 | 27347 | 609959 | 3547573 | 16.7358 | min EUI | min EUI
| TMY7 WA | 393159 | 1187641 | 690919 | 67074 | 482612 | 377016 | 0 | 75807 | 148866 | 27347 | 609959 | 3450441 | 16.2776 | 16.0652 | 16.0652
| TMY15 WA | 348415 | 1253922 | 690919 | 66928 | 482612 | 378429 | 0 | 80038 | 148866 | 27347 | 609959 | 3477476 | 16.4051 | variance | variance
| XMY Min WA | 1659441 | 592616 | 690919 | 70485 | 482612 | 396913 | 0 | 37827 | 148866 | 27347 | 609959 | 4107026 | 19.375 | 20.6% | 4.174%
| XMY Max WA | 76578 | 1662032 | 690919 | 66074 | 482612 | 426380 | 0 | 106087 | 148866 | 27347 | 609959 | 3686895 | 17.3931
2B - Phoenix | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 327476 | 1272034 | 995949 | 63125 | 804355 | 466713 | 0 | 81194 | 148866 | 27347 | 609959 | 4187059 | 19.7526 | max EUI | max EUI
| TMY3 DOE | 248428 | 1410611 | 995949 | 63744 | 804355 | 493987 | 0 | 90039 | 148866 | 27347 | 609959 | 4283326 | 20.2068 | 21.1585 | 20.2068
| TMY3 WA | 231950 | 1413414 | 995949 | 65367 | 804355 | 489149 | 0 | 90218 | 148866 | 27347 | 609959 | 4266615 | 20.1279 | min EUI | min EUI
| TMY7 WA | 266275 | 1283201 | 995949 | 65086 | 804355 | 462980 | 0 | 81906 | 12375 | 27347 | 609959 | 3999474 | 18.8677 | 18.8677 | 18.8677
| TMY15 WA | 279150 | 1357043 | 995949 | 65187 | 804355 | 481969 | 0 | 86620 | 148866 | 27347 | 609959 | 4246486 | 20.033 | variance | variance
| XMY Min WA | 941278 | 734022 | 995949 | 65293 | 804355 | 409887 | 0 | 46852 | 148866 | 27347 | 609959 | 4173849 | 19.6903 | 11.34% | 6.627%
| XMY Max WA | 104439 | 1693539 | 995949 | 64561 | 804355 | 537911 | 0 | 108098 | 148866 | 27347 | 609959 | 4485065 | 21.1585
3A - Atlanta | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1994166 | 747874 | 995949 | 63980 | 804355 | 515077 | 7945 | 47737 | 148866 | 27347 | 609959 | 5353296 | 25.2544 | max EUI | max EUI
| TMY3 DOE | 1820376 | 809306 | 995949 | 65054 | 804355 | 516006 | 7305 | 51658 | 148866 | 27347 | 609959 | 5246222 | 24.7492 | 36.3804 | 25.2544
| TMY3 WA | 1197384 | 969907 | 995949 | 67970 | 804355 | 517249 | 5096 | 61909 | 148866 | 27347 | 609959 | 4796032 | 22.6255 | min EUI | min EUI
| TMY7 WA | 1566907 | 937781 | 995949 | 68096 | 804355 | 540541 | 6555 | 59858 | 148866 | 27347 | 609959 | 5156255 | 24.3248 | 19.5103 | 22.6255
| TMY15 WA | 1339508 | 959939 | 995949 | 67696 | 804355 | 531272 | 5634 | 61273 | 148866 | 27347 | 609959 | 4941839 | 23.3133 | variance | variance
| XMY Min WA | 4355213 | 637130 | 995949 | 67484 | 804355 | 617814 | 16903 | 40668 | 148866 | 27347 | 609959 | 7711729 | 36.3804 | 68.16% | 10.62%
| XMY Max WA | 420529 | 1114768 | 995949 | 68177 | 804355 | 482724 | 1816 | 71155 | 148866 | 27347 | 609959 | 4135686 | 19.5103
3B - Las Vegas | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1178207 | 1084227 | 995949 | 62884 | 804355 | 571913 | 4730 | 69206 | 148866 | 27347 | 609959 | 4947684 | 23.3409 | max EUI | max EUI
| TMY3 DOE | 1207868 | 1127359 | 995949 | 63904 | 804355 | 581615 | 4858 | 71959 | 148866 | 27347 | 609959 | 5034080 | 23.7485 | 30.071 | 23.8726
| TMY3 WA | 1136248 | 1184959 | 995949 | 65126 | 804355 | 594106 | 4625 | 75636 | 148866 | 27347 | 609959 | 5037217 | 23.7633 | min EUI | min EUI
| TMY7 WA | 1183832 | 1110677 | 995949 | 65081 | 804355 | 577944 | 4838 | 70894 | 148866 | 27347 | 609959 | 4989783 | 23.5395 | 22.5801 | 23.3409
| TMY15 WA | 1221645 | 1132911 | 995949 | 65108 | 804355 | 586898 | 4995 | 72313 | 148866 | 27347 | 609959 | 5060387 | 23.8726 | variance | variance
| XMY Min WA | 2983726 | 719141 | 995949 | 64998 | 804355 | 572589 | 11424 | 45903 | 148866 | 27347 | 609959 | 6374298 | 30.071 | 31.54% | 2.239%
| XMY Max WA | 599188 | 1448933 | 995949 | 64775 | 804355 | 602123 | 2404 | 92485 | 148866 | 27347 | 609959 | 4786425 | 22.5801
3C - San Francisco | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 1718009 | 348437 | 995949 | 64750 | 804355 | 482662 | 6741 | 22241 | 148866 | 27347 | 609959 | 4619357 | 21.792 | max EUI | max EUI
| TMY3 DOE | 1439783 | 331706 | 995949 | 65376 | 804355 | 439873 | 5640 | 21173 | 148866 | 27347 | 609959 | 4280068 | 20.1914 | 27.1809 | 21.792
| TMY3 WA | 1024576 | 351849 | 995949 | 66935 | 804355 | 403739 | 4114 | 22458 | 148866 | 27347 | 609959 | 3850188 | 18.1634 | min EUI | min EUI
| TMY7 WA | 1544892 | 324334 | 995949 | 67750 | 804355 | 457687 | 6134 | 20702 | 148866 | 27347 | 609959 | 4398016 | 20.7478 | 16.982 | 18.1634
| TMY15 WA | 1333382 | 352942 | 995949 | 67421 | 804355 | 448578 | 5337 | 22528 | 148866 | 27347 | 609959 | 4206705 | 19.8453 | variance | variance
| XMY Min WA | 2714566 | 366334 | 995949 | 66070 | 804355 | 604243 | 10561 | 23383 | 148866 | 27347 | 609959 | 5761674 | 27.1809 | 50.51% | 17.97%
| XMY Max WA | 708824 | 427142 | 995949 | 65935 | 804355 | 391291 | 2791 | 27264 | 148866 | 27347 | 609959 | 3599764 | 16.982
4A - Baltimore | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 3292246 | 718493 | 995949 | 65590 | 804355 | 583073 | 12965 | 45861 | 148866 | 27347 | 609959 | 6694745 | 31.5827 | max EUI | max EUI
| TMY3 DOE | 3021611 | 728363 | 995949 | 65750 | 804355 | 572942 | 11986 | 46491 | 148866 | 27347 | 609959 | 6423660 | 30.3039 | 43.2083 | 31.5827
| TMY3 WA | 2077545 | 866953 | 995949 | 68515 | 804355 | 565156 | 8677 | 55337 | 148866 | 27347 | 609959 | 5618700 | 26.5064 | min EUI | min EUI
| TMY7 WA | 2475844 | 817382 | 995949 | 68783 | 804355 | 572625 | 10187 | 52173 | 148866 | 27347 | 609959 | 5973511 | 28.1803 | 21.7771 | 26.5064
| TMY15 WA | 2222634 | 855293 | 995949 | 68130 | 804355 | 569064 | 9197 | 54593 | 148866 | 27347 | 609959 | 5755428 | 27.1514 | variance | variance
| XMY Min WA | 5779121 | 596882 | 995949 | 69648 | 804355 | 677319 | 21495 | 38099 | 148866 | 27347 | 609959 | 9159081 | 43.2083 | 70.72% | 16.75%
| XMY Max WA | 912510 | 1074045 | 995949 | 68839 | 804355 | 511835 | 3899 | 68556 | 148866 | 27347 | 609959 | 4616201 | 21.7771
4B - Albuquerque | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 2825211 | 606570 | 995949 | 63879 | 804355 | 567469 | 11194 | 38717 | 148866 | 27347 | 609959 | 6089557 | 28.7277 | max EUI | max EUI
| TMY3 DOE | 2614471 | 608389 | 995949 | 64332 | 804355 | 563012 | 10458 | 38833 | 148866 | 27347 | 609959 | 5876012 | 27.7203 | 41.2895 | 29.0734
| TMY3 WA | 2319752 | 730977 | 995949 | 65054 | 804355 | 579055 | 9642 | 46658 | 148866 | 27347 | 609959 | 5727655 | 27.0204 | min EUI | min EUI
| TMY7 WA | 2779515 | 695653 | 995949 | 65156 | 804355 | 590251 | 11341 | 44403 | 148866 | 27347 | 609959 | 6162836 | 29.0734 | 24.003 | 27.0204
| TMY15 WA | 2663392 | 708420 | 995949 | 65158 | 804355 | 585062 | 10859 | 45218 | 148866 | 27347 | 609959 | 6054626 | 28.5629 | variance | variance
| XMY Min WA | 5455159 | 533270 | 995949 | 65196 | 804355 | 667864 | 20303 | 34038 | 148866 | 27347 | 609959 | 8752347 | 41.2895 | 62.36% | 7.406%
| XMY Max WA | 1596694 | 840111 | 995949 | 64692 | 804355 | 549788 | 6600 | 53624 | 148866 | 27347 | 609959 | 5088026 | 24.003
4C - Portland | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 2871401 | 451619 | 995949 | 66495 | 804355 | 567982 | 11485 | 28827 | 148866 | 27347 | 609959 | 5974326 | 28.1841 | max EUI | max EUI
| TMY3 DOE | 2684021 | 452065 | 995949 | 67250 | 804355 | 551223 | 10817 | 28855 | 148866 | 27347 | 609959 | 5770748 | 27.2237 | 44.3609 | 29.7909
| TMY3 WA | 2512056 | 533556 | 995949 | 71638 | 804355 | 570680 | 10377 | 34057 | 148866 | 27347 | 609959 | 5708881 | 26.9319 | min EUI | min EUI
| TMY7 WA | 3038817 | 568841 | 995949 | 70483 | 804355 | 611663 | 12295 | 36309 | 148866 | 27347 | 609959 | 6314925 | 29.7909 | 22.8261 | 26.9319
| TMY15 WA | 2761402 | 558877 | 995949 | 70857 | 804355 | 593470 | 11333 | 35673 | 148866 | 27347 | 609959 | 6008129 | 28.3436 | variance | variance
| XMY Min WA | 6028669 | 509487 | 995949 | 69853 | 804355 | 763730 | 22636 | 32520 | 148866 | 27347 | 609959 | 9403412 | 44.3609 | 79.1% | 10.5%
| XMY Max WA | 1550490 | 666599 | 995949 | 71823 | 804355 | 524055 | 6524 | 42549 | 148866 | 27347 | 609959 | 4838557 | 22.8261
5A - Chicago | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 4737243 | 676306 | 995949 | 65392 | 804355 | 648432 | 18595 | 43168 | 148866 | 27347 | 609959 | 8165653 | 38.5218 | max EUI | max EUI
| TMY3 DOE | 4622508 | 684242 | 995949 | 66056 | 804355 | 638240 | 18228 | 43675 | 148866 | 27347 | 609959 | 8049466 | 37.9737 | 54.8701 | 38.5218
| TMY3 WA | 3144625 | 723942 | 995949 | 69087 | 804355 | 592025 | 13070 | 46209 | 148866 | 27347 | 609959 | 6565475 | 30.9729 | min EUI | min EUI
| TMY7 WA | 3980111 | 706427 | 995949 | 68738 | 804355 | 624734 | 16173 | 45091 | 148866 | 27347 | 609959 | 7417791 | 34.9937 | 25.2324 | 30.9729
| TMY15 WA | 3637210 | 722923 | 995949 | 68630 | 804355 | 615462 | 14808 | 46144 | 148866 | 27347 | 609959 | 7081694 | 33.4082 | variance | variance
| XMY Min WA | 8151034 | 591716 | 995949 | 67871 | 804355 | 775962 | 30228 | 37769 | 148866 | 27347 | 609959 | 11631097 | 54.8701 | 78.05% | 19.88%
| XMY Max WA | 1885912 | 820226 | 995949 | 69607 | 804355 | 535920 | 8101 | 52355 | 148866 | 27347 | 609959 | 5348638 | 25.2324
5B - Boulder | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 4720389 | 551620 | 690919 | 65151 | 482612 | 620254 | 19005 | 35210 | 148866 | 27347 | 609959 | 7361373 | 34.7276 | max EUI | max EUI
| TMY3 DOE | 3938358 | 565159 | 995949 | 65421 | 804355 | 605218 | 16080 | 36074 | 148866 | 27347 | 609959 | 7202827 | 33.9796 | 61.9112 | 38.1786
| TMY3 WA | 4719317 | 583165 | 995949 | 65757 | 804355 | 650143 | 19509 | 37223 | 148866 | 27347 | 609959 | 8051631 | 37.9839 | min EUI | min EUI
| TMY7 WA | 4752617 | 589904 | 995949 | 65788 | 804355 | 650972 | 19455 | 37653 | 148866 | 27347 | 609959 | 8092906 | 38.1786 | 29.1557 | 33.9796
| TMY15 WA | 4601313 | 590019 | 995949 | 65617 | 804355 | 644206 | 19038 | 37661 | 148866 | 27347 | 609959 | 7934371 | 37.4307 | variance | variance
| XMY Min WA | 9620279 | 550219 | 995949 | 66908 | 804355 | 838747 | 35827 | 35120 | 148866 | 27347 | 609959 | 13123617 | 61.9112 | 96.4% | 12.36%
| XMY Max WA | 2852800 | 656913 | 995949 | 64928 | 804355 | 575106 | 12079 | 41931 | 148866 | 27347 | 609959 | 6180274 | 29.1557
5C - Vancouver | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
[15 empty] | max EUI | max EUI
| CWEC | 3597409 | 300010 | 995949 | 71215 | 804355 | 649829 | 14453 | 19150 | 148866 | 27347 | 609959 | 6628583 | 31.2706 | 44.6809 | 31.7975
| TMY3 WA | 2831179 | 328681 | 995949 | 71305 | 804355 | 607719 | 11587 | 20980 | 148866 | 27347 | 609959 | 5847968 | 27.588 | min EUI | min EUI
| TMY7 WA | 3692942 | 304617 | 995949 | 71985 | 804355 | 659953 | 14816 | 19444 | 148866 | 27347 | 609959 | 6740274 | 31.7975 | 24.4761 | 27.588
| TMY15 WA | 3315524 | 312951 | 995949 | 71902 | 804355 | 642088 | 13523 | 19976 | 148866 | 27347 | 609959 | 6352481 | 29.9681 | variance | variance
| XMY Min WA | 6236151 | 321838 | 995949 | 70096 | 804355 | 822981 | 23111 | 20543 | 148866 | 27347 | 609959 | 9471237 | 44.6809 | 64.61% | 13.46%
| XMY Max WA | 2198712 | 342050 | 995949 | 72487 | 804355 | 567472 | 9244 | 21833 | 148866 | 27347 | 609959 | 5188315 | 24.4761
6A - Minneapolis | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 6094314 | 649762 | 995949 | 65505 | 804355 | 649088 | 23273 | 41474 | 148866 | 27347 | 609959 | 9499933 | 44.8163 | max EUI | max EUI
| TMY3 DOE | 5929808 | 651421 | 995949 | 66358 | 804355 | 652944 | 23104 | 41580 | 148866 | 27347 | 609959 | 9341732 | 44.07 | 64.9925 | 44.8163
| TMY3 WA | 4029611 | 724085 | 995949 | 69312 | 804355 | 592725 | 16460 | 46218 | 148866 | 27347 | 609959 | 7454928 | 35.1689 | min EUI | min EUI
| TMY7 WA | 5476296 | 685220 | 995949 | 69112 | 804355 | 639329 | 21630 | 43737 | 148866 | 27347 | 609959 | 8911841 | 42.0419 | 29.5363 | 35.1689
| TMY15 WA | 4684275 | 716750 | 995949 | 69256 | 804355 | 614555 | 18661 | 45750 | 148866 | 27347 | 609959 | 8125764 | 38.3336 | variance | variance
| XMY Min WA | 10251486 | 597331 | 995949 | 68745 | 804355 | 807576 | 37002 | 38128 | 148866 | 27347 | 609959 | 13776785 | 64.9925 | 80.45% | 21.89%
| XMY Max WA | 2700736 | 890513 | 995949 | 69510 | 804355 | 555549 | 11301 | 56841 | 148866 | 27347 | 609959 | 6260967 | 29.5363
6B - Helena | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 5827702 | 497381 | 995949 | 65365 | 804355 | 631953 | 23225 | 31748 | 148866 | 27347 | 609959 | 9053891 | 42.7121 | max EUI | max EUI
| TMY3 DOE | 5620008 | 488189 | 995949 | 65928 | 804355 | 619440 | 22705 | 31161 | 148866 | 27347 | 609959 | 8823948 | 41.6273 | 70.5398 | 42.7121
| TMY3 WA | 5228703 | 587399 | 995949 | 67579 | 804355 | 636939 | 21833 | 37494 | 148866 | 27347 | 609959 | 8556464 | 40.3654 | min EUI | min EUI
| TMY7 WA | 34960 | 1678923 | 995949 | 66270 | 804355 | 455837 | 159 | 107165 | 148866 | 27347 | 609959 | 4319831 | 20.379 | 20.379 | 20.379
| TMY15 WA | 5545707 | 556268 | 995949 | 67653 | 804355 | 642849 | 22930 | 35506 | 148866 | 27347 | 609959 | 8847430 | 41.7381 | variance | variance
| XMY Min WA | 11455356 | 525693 | 995949 | 67907 | 804355 | 851006 | 42636 | 33555 | 148866 | 27347 | 609959 | 14952670 | 70.5398 | 120.5% | 53.65%
| XMY Max WA | 3782144 | 631127 | 995949 | 66833 | 804355 | 567893 | 15911 | 40285 | 148866 | 27347 | 609959 | 7080710 | 33.4035
7 - Duluth | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 7904738 | 516425 | 995949 | 65410 | 804355 | 707403 | 30293 | 32963 | 148866 | 27347 | 609959 | 11233749 | 52.9956 | max EUI | max EUI
| TMY3 DOE | 7494720 | 504265 | 995949 | 66252 | 804355 | 680202 | 28999 | 32187 | 148866 | 27347 | 609959 | 10783142 | 50.8699 | 70.1786 | 52.9956
| TMY3 WA | 4916319 | 575656 | 995949 | 70186 | 804355 | 602717 | 20149 | 36744 | 148866 | 27347 | 609959 | 8198288 | 38.6757 | min EUI | min EUI
| TMY7 WA | 6287201 | 555010 | 995949 | 70105 | 804355 | 644561 | 24980 | 35426 | 148866 | 27347 | 609959 | 9593800 | 45.2591 | 32.107 | 38.6757
| TMY15 WA | 5452677 | 561769 | 995949 | 69756 | 804355 | 616403 | 21995 | 35858 | 148866 | 27347 | 609959 | 8734975 | 41.2076 | variance | variance
| XMY Min WA | 11401136 | 514934 | 995949 | 69146 | 804355 | 840028 | 41474 | 32868 | 148866 | 27347 | 609959 | 14876103 | 70.1786 | 74.84% | 28.15%
| XMY Max WA | 3480285 | 677805 | 995949 | 70985 | 804355 | 542489 | 14528 | 43264 | 148866 | 27347 | 609959 | 6805873 | 32.107
8 - Fairbanks | Weather File | Heating (kBtu) | Cooling (kBtu) | Interior Lighting (kBtu) | Exterior Lighting (kBtu) | Receptacle Equipment (kBtu) | Interior Fans (kBtu) | Distribution Pumps Energy (kBtu) | Heat Rejection (kBtu) | DHW (kBtu) | Refrigeration (kBtu) | Cooking (kBtu) | Total (kBtu) | EUI
| TMY2 DOE | 11721461 | 362899 | 995949 | 72812 | 804355 | 777070 | 43691 | 23164 | 148866 | 27347 | 609959 | 14977614 | 70.6575 | max EUI | max EUI
| TMY3 DOE | 10720387 | 368776 | 995949 | 73251 | 804355 | 741900 | 40973 | 23539 | 148866 | 27347 | 609959 | 13945343 | 65.7877 | 94.2616 | 70.6575
| TMY3 WA | 8171619 | 411545 | 995949 | 74037 | 804355 | 687374 | 32952 | 26269 | 148866 | 27347 | 609959 | 11380313 | 53.6871 | min EUI | min EUI
| TMY7 WA | 9943076 | 396728 | 995949 | 74073 | 804355 | 742344 | 39184 | 25323 | 148866 | 27347 | 609959 | 13197245 | 62.2585 | 44.6737 | 53.6871
| TMY15 WA | 9173204 | 408059 | 995949 | 74199 | 804355 | 711735 | 36320 | 26046 | 148866 | 27347 | 609959 | 12406080 | 58.5261 | variance | variance
| XMY Min WA | 16498357 | 385427 | 995949 | 75106 | 804355 | 961985 | 59100 | 24602 | 148866 | 27347 | 609959 | 19981094 | 94.2616 | 75.38% | 25.8%
| XMY Max WA | 6277913 | 453019 | 995949 | 73843 | 804355 | 633102 | 26387 | 28916 | 148866 | 27347 | 609959 | 9469697 | 44.6737
1A - Miami
2A - Houston
2B - Phoenix
3A - Atlanta
3B - Las Vegas
3C - San Francisco
4A - Baltimore
4B - Albuquerque
4C - Portland
5A - Chicago
5B - Boulder
5C - Vancouver
6A - Minneapolis
6B - Helena
7 - Duluth
8 - Fairbanks

## pslpd Additional Indicators
[14 empty] | Predicted Percentage Dissatisfied | [9 empty] | Peak Heating Load | [9 empty] | Peak Cooling Load
Climate Zone | Climate File | PPD - Floor 1 | PPD - Floor 2 | PPD - Kitchen | PPD - Gym | PPD - Auditorium | Unmet Hours (Heating) | Unmet Hours (Cooling) | UH Compliance | Peak Heating Load | Peak Cooling Load | Overheating Risk | EUI | Climate | [9 empty] | Climate | [9 empty] | Climate
1A | TMY2 | [5 empty] | 0 | 1 | 1 |  |  |  |  | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 1A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3 | [5 empty] | 2 | 1 | 3 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 34 | 07:30,23/Jan | 99 | 16:30,10/Sep | 91 |  | Heating plant sensible load | ASHRAE ZONING - FLOOR 1 | RL.htg | Load (Btu/h) | 1347474 | 12:00, January | 1347474 | 12:00, January | 1347474 |  | Cooling plant sensible load | ASHRAE ZONING - FLOOR 1 | RL.clg | Load (Btu/h) | 0 | 00:30, May | 836799 | 06:30, July | 242226
| TMY3WA | [5 empty] | 0 | 0 | 0 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 07:30,23/Jan | 60 | 14:30,10/Sep | 35 | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY7WA | [5 empty] | 0 | 1 | 1 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 60 | 00:30,01/Apr | 100 | 14:30,22/Mar | 95 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3817965 | 12:00, January | 3817965 | 12:00, January | 3817965 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 2088790 | 14:30, September | 706081
| TMY15WA | [5 empty] | 0 | 2 | 2 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 07:30,31/Mar | 67 | 15:30,22/Aug | 30 | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| XMY MAX | [5 empty] | 0 | 0 | 0 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 08:30,14/Jan | 59 | 07:30,05/Sep | 22 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3335691 | 12:00, January | 3335691 | 12:00, January | 3335691 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 33472 | 04:30, May | 2663299 | 13:30, September | 1158642
| XMYMIN | [5 empty] | 20 | 2 | 22 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 6 | 14:30,23/Jan | 62 | 03:30,17/Aug | 28 | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
2A | TMY2 | [5 empty] | 6 | 2 | 8 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 6 | 05:30,04/Jan | 99 | 16:30,10/Sep | 86 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4088501 | 12:00, January | 4088501 | 12:00, January | 4088501 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1750283 | 14:30, September | 596672
| TMY3 | [5 empty] | 1 | 2 | 3 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 06:30,29/Dec | 60 | 14:30,10/Sep | 32 | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3WA | [5 empty] | 1 | 8 | 9 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 18 | 07:30,03/Jan | 100 | 15:30,02/Apr | 93 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3619627 | 12:00, January | 3619627 | 12:00, January | 3619627 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 7055 | 04:30, May | 2283118 | 06:30, July | 948956
| TMY7WA | [5 empty] | 0 | 2 | 2 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 02:30,29/Jan | 67 | 17:30,17/Jul | 26 | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY15WA | [5 empty] | 0 | 3 | 3 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 08:30,12/Mar | 59 | 07:30,05/Sep | 19 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3224919 | 12:00, January | 3224919 | 12:00, January | 3224919 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1134247 | 16:30, September | 233197
| XMY MAX | [5 empty] | 0 | 14 | 14 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 13:30,02/Jan | 64 | 06:30,03/Jul | 25 | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| XMYMIN | [5 empty] | 23 | 2 | 25 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 6 | 05:30,04/Feb | 99 | 16:30,22/Sep | 83 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4186155 | 12:00, January | 4186155 | 12:00, January | 4186155 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1834987 | 14:30, September | 609641
2B | TMY2 | [5 empty] | 4 | 10 | 14 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 02:30,15/Dec | 56 | 14:30,09/Sep | 30 | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3 | [5 empty] | 0 | 19 | 19 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 31 | 05:30,04/Feb | 100 | 16:30,17/May | 91 |  | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 3979020 | 12:00, January | 3979020 | 12:00, January | 3979020 |  | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1620069 | 14:30, September | 492266
| TMY3WA | [5 empty] | 0 | 22 | 22 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 01:30,20/Mar | 66 | 12:30,02/Oct | 24 | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY7WA | [5 empty] | 0 | 17 | 17 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 08:30,14/Dec | 60 | 03:30,11/Sep | 18 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3717431 | 12:00, January | 3717431 | 12:00, January | 3717431 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1703772 | 14:30, September | 545748
| TMY15WA | [5 empty] | 2 | 13 | 15 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 20:30,20/Dec | 63 | 01:30,30/Oct | 24 | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| XMY MAX | [5 empty] | 0 | 25 | 25 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 6 | 01:30,13/Jan | 99 | 16:30,01/Sep | 83 |  | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 4783322 | 12:00, January | 4783322 | 12:00, January | 4783322 |  | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1715606 | 14:30, September | 547479+BF403
| XMYMIN | [5 empty] | 55 | 3 | 58 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 04:30,31/Jan | 52 | 16:30,09/Sep | 30 | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
3A | TMY2 | [5 empty] | 47 | 5 | 52 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 15 | 04:30,04/Jan | 100 | 15:30,19/May | 91 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 4593129 | 12:00, January | 4593129 | 12:00, January | 4593129 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1623303 | 14:30, September | 435957
| TMY3 | [5 empty] | 29 | 7 | 36 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 01:30,20/Mar | 67 | 10:30,25/Jul | 24 | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3WA | [5 empty] | 0 | 6 | 6 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 08:30,09/Feb | 58 | 04:30,07/Oct | 18 |  | Heating plant sensible load | 46 rooms | RL.htg | Load (Btu/h) | 3909844 | 12:00, January | 3909844 | 12:00, January | 3909844 |  | Cooling plant sensible load | 46 rooms | RL.clg | Load (Btu/h) | 0 | 00:30, May | 1097704 | 16:30, September | 244993
| TMY7WA | [5 empty] | 4 | 3 | 7 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 16:30,03/Jan | 63 | 04:30,23/Aug | 24 | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY15WA | [5 empty] | 0 | 8 | 8 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 6 | 18:30,09/Jan | 99 | 16:30,07/Oct | 88 |  | Heating plant sensible load | 46 rooms | ROOMLOADS_TMY2.htg | Load (Btu/h) | 5063981 | 12:00, January | 5063981 | 12:00, January | 5063981 |  | Cooling plant sensible load | 46 rooms | ROOMLOADS_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1659937 | 14:30, September | 552584
| XMY MAX | [5 empty] | 0 | 12 | 12 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 01:30,04/Jan | 60 | 14:30,07/Oct | 33 | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| XMYMIN | [5 empty] | 188 | 2 | 190 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 31 | 07:30,09/Jan | 100 | 15:30,26/Mar | 94 |  | Heating plant sensible load | 46 rooms | ROOMLOAD_TMY2.htg | Load (Btu/h) | 5141729 | 12:00, January | 5141729 | 12:00, January | 5141729 |  | Cooling plant sensible load | 46 rooms | ROOMLOAD_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1535761 | 16:30, September | 413026
3B | TMY2 | [5 empty] | 15 | 13 | 28 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 03:30,03/Feb | 68 | 15:30,03/Jul | 28 | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3 | [5 empty] | 10 | 16 | 26 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 08:30,28/Dec | 59 | 04:30,25/Sep | 20 |  | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 5145132 | 12:00, January | 5145132 | 12:00, January | 5145132 |  | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1362498 | 14:30, September | 385377
| TMY3WA | [5 empty] | 8 | 15 | 23 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 17:30,04/Jan | 63 | 04:30,28/Oct | 27 | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY7WA | [5 empty] | 14 | 9 | 23 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 00:30,08/Mar | 99 | 16:30,08/Sep | 66 |  | Heating plant sensible load | 46 rooms | RL_TMY2.htg | Load (Btu/h) | 5939305 | 12:00, January | 5939305 | 12:00, January | 5939305 |  | Cooling plant sensible load | 46 rooms | RL_TMY2.clg | Load (Btu/h) | 0 | 00:30, May | 1242278 | 16:30, May | 294945
| TMY15WA | [5 empty] | 10 | 16 | 26 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 07:30,06/Dec | 55 | 15:30,08/Sep | 23
| XMY MAX | [5 empty] | 0 | 23 | 23 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 6 | 16:30,24/Jan | 100 | 16:30,28/Apr | 81
| XMYMIN | [5 empty] | 115 | 0 | 115 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 03:30,08/Apr | 67 | 09:30,25/Jul | 19
3C | TMY2 | [5 empty] | 6 | 2 | 8 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 10:30,20/Nov | 56 | 00:30,26/Jul | 14
| TMY3 | [5 empty] | 2 | 2 | 4 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 17:30,11/Jan | 62 | 00:30,14/Aug | 18
| TMY3WA | [5 empty] | 0 | 8 | 8 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 77 | 07:30,15/Jan | 100 | 15:30,01/Sep | 93
| TMY7WA | [5 empty] | 2 | 2 | 4 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 20 | 08:30,16/Jan | 63 | 14:30,03/Sep | 38
| TMY15WA | [5 empty] | 0 | 5 | 5 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 85 | 01:30,18/Apr | 100 | 15:30,08/Mar | 96
| XMY MAX | [5 empty] | 0 | 22 | 22 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 6 | 11:30,20/Dec | 68 | 16:30,15/Aug | 33
| XMYMIN | [5 empty] | 36 | 0 | 36 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 11:30,04/Dec | 61 | 02:30,17/Sep | 24
4A | TMY2 | [5 empty] | 106 | 159 | 265 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 6 | 14:30,19/Dec | 63 | 18:30,18/Jul | 30
| TMY3 | [5 empty] | 96 | 133 | 229 |  |  |  |  | 2A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY3WA | [5 empty] | 11 | 196 | 207 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 19 | 05:30,18/Jan | 100 | 16:30,13/Sep | 85
| TMY7WA | [5 empty] | 25 | 122 | 147 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 07:30,22/Jan | 56 | 14:30,28/May | 27
| TMY15WA | [5 empty] | 26 | 192 | 218 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 23 | 05:30,27/Dec | 100 | 15:30,09/Apr | 87
| XMY MAX | [5 empty] | 1 | 173 | 174 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 11:30,27/Dec | 69 | 16:30,18/Jul | 21
| XMYMIN | [5 empty] | 371 | 109 | 480 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 11:30,27/Feb | 56 | 00:30,16/Aug | 15
4B | TMY2 | [5 empty] | 131 | 1219 | 1350 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 11:30,16/Jan | 63 | 05:30,21/Aug | 22
| TMY3 | [5 empty] | 112 | 1270 | 1382 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 8 | 05:30,21/Dec | 100 | 16:30,28/Sep | 88
| TMY3WA | [5 empty] | 59 | 1758 | 1817 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 08:30,19/Jan | 61 | 15:30,20/Sep | 29
| TMY7WA | [5 empty] | 118 | 1490 | 1608 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 8 | 06:30,20/Dec | 100 | 15:30,11/May | 90
| TMY15WA | [5 empty] | 122 | 1754 | 1876 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 05:30,21/Feb | 67 | 11:30,18/Jul | 23
| XMY MAX | [5 empty] | 14 | 2341 | 2355 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 11:30,07/Feb | 58 | 03:30,28/Sep | 16
| XMYMIN | [5 empty] | 539 | 484 | 1023 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 12:30,25/Dec | 63 | 05:30,07/Jul | 24
4C | TMY2 | [5 empty] | 46 | 118 | 164 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 18 | 05:30,15/Feb | 100 | 15:30,03/Aug | 82
| TMY3 | [5 empty] | 44 | 57 | 101 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 21:30,09/Jan | 51 | 14:30,21/Sep | 25
| TMY3WA | [5 empty] | 16 | 218 | 234 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 16 | 06:30,12/Feb | 100 | 16:30,11/May | 85
| TMY7WA | [5 empty] | 52 | 315 | 367 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 01:30,17/Mar | 67 | 10:30,25/Jul | 20
| TMY15WA | [5 empty] | 28 | 287 | 315 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 09:30,20/Mar | 53 | 21:30,01/Aug | 14
| XMY MAX | [5 empty] | 0 | 866 | 866 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 11:30,02/Jan | 64 | 07:30,04/Jul | 21
| XMYMIN | [5 empty] | 386 | 1 | 387 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 10 | 06:30,14/Jan | 100 | 16:30,16/Sep | 81
5A | TMY2 | [5 empty] | 208 | 89 | 297 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 08:30,23/Dec | 50 | 14:30,24/Sep | 25
| TMY3 | [5 empty] | 219 | 76 | 295 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 8 | 06:30,11/Jan | 100 | 14:30,18/May | 84
| TMY3WA | [5 empty] | 51 | 83 | 134 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 12:30,01/Feb | 67 | 10:30,17/Jul | 20
| TMY7WA | [5 empty] | 100 | 66 | 166 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 10:30,09/Jan | 51 | 04:30,05/Jul | 13
| TMY15WA | [5 empty] | 98 | 84 | 182 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 20:30,12/Jan | 64 | 07:30,11/Jul | 21
| XMY MAX | [5 empty] | 5 | 154 | 159 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 27 | 05:30,30/Dec | 100 | 16:30,13/Sep | 86
| XMYMIN | [5 empty] | 785 | 9 | 794 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 05:30,08/Mar | 56 | 14:30,14/Sep | 27
5B | TMY2 | [5 empty] | 265 | 1057 | 1322 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 23 | 05:30,27/Dec | 100 | 12:30,29/Apr | 88
| TMY3 | [5 empty] | 231 | 1077 | 1308 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 11:30,27/Dec | 68 | 08:30,06/Jun | 21
| TMY3WA | [5 empty] | 230 | 839 | 1069 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 13:30,10/Jan | 56 | 00:30,16/Aug | 15
| TMY7WA | [5 empty] | 295 | 867 | 1162 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 13:30,11/Dec | 66 | 07:30,06/Jun | 23
| TMY15WA | [5 empty] | 237 | 914 | 1151 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 7 | 17:30,18/Jan | 99 | 16:30,29/Jul | 63
| XMY MAX | [5 empty] | 73 | 1689 | 1762 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 04:30,19/Apr | 48 | 16:30,09/Sep | 21
| XMYMIN | [5 empty] | 1333 | 85 | 1418 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 7 | 17:30,13/Feb | 100 | 15:30,14/Jun | 69
5C | TMY2 | [5 empty] | 54 | 9 | 63 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 12:30,19/Jan | 67 | 18:30,18/Jul | 18
| TMY3 | [5 empty] | 56 | 9 | 65 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 12:30,30/Oct | 48 | 19:30,13/Jun | 12
| TMY3WA | [5 empty] | 10 | 115 | 125 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 18:30,16/Feb | 61 | 22:30,08/Aug | 16
| TMY7WA | [5 empty] | 33 | 32 | 65 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 72 | 00:30,18/Jan | 100 | 13:30,01/Sep | 94
| TMY15WA | [5 empty] | 16 | 29 | 45 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 10 | 00:30,18/Jan | 70 | 15:30,03/Sep | 35
| XMY MAX | [5 empty] | 0 | 356 | 356 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 70 | 00:30,18/Jan | 100 | 14:30,29/Mar | 95
| XMYMIN | [5 empty] | 365 | 0 | 365 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 6 | 10:30,15/Jan | 67 | 13:30,08/Aug | 28
6A | TMY2 | [5 empty] | 491 | 96 | 587 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 12:30,07/Feb | 59 | 03:30,28/Sep | 19
| TMY3 | [5 empty] | 404 | 150 | 554 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 6 | 09:30,25/Dec | 63 | 04:30,12/Jun | 27
| TMY3WA | [5 empty] | 106 | 195 | 301 |  |  |  |  | 2B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
| TMY7WA | [5 empty] | 335 | 181 | 516 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,11/Mar | 58 | 02:30,23/Aug | 17
| TMY15WA | [5 empty] | 278 | 260 | 538 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 22:30,14/Dec | 51 | 13:30,02/Sep | 21
| XMY MAX | [5 empty] | 32 | 449 | 481 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,02/Dec | 59 | 14:30,28/Aug | 19
| XMYMIN | [5 empty] | 1079 | 92 | 1171 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 21:30,19/Jan | 62 | 13:30,01/Aug | 17
6B | TMY2 | [5 empty] | 426 | 686 | 1112 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 10:30,02/Jan | 53 | 21:30,15/Aug | 14
| TMY3 | [5 empty] | 344 | 645 | 989 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 08:30,26/Jan | 58 | 06:30,11/Jul | 16
| TMY3WA | [5 empty] | 214 | 947 | 1161 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 06:30,25/Nov | 55 | 14:30,25/Jul | 19
| TMY7WA | [5 empty] | 0 | 2153 | 2153 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 01:30,18/Feb | 52 | 13:30,09/Sep | 23
| TMY15WA | [5 empty] | 242 | 797 | 1039 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 06:30,12/Nov | 57 | 15:30,22/Aug | 20
| XMY MAX | [5 empty] | 97 | 1513 | 1610 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 02:30,22/Feb | 61 | 13:30,15/Aug | 19
| XMYMIN | [5 empty] | 1388 | 81 | 1469 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 16:30,18/Dec | 54 | 07:30,15/Aug | 15
7 | TMY2 | [5 empty] | 681 | 64 | 745 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 20:30,03/Dec | 57 | 05:30,15/Aug | 18
| TMY3 | [5 empty] | 613 | 65 | 678 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,11/Nov | 59 | 04:30,21/Jul | 20
| TMY3WA | [5 empty] | 198 | 152 | 350 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 09:30,22/Dec | 52 | 13:30,03/Sep | 23
| TMY7WA | [5 empty] | 407 | 145 | 552 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 06:30,28/Oct | 58 | 04:30,21/Jul | 22
| TMY15WA | [5 empty] | 290 | 103 | 393 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 00:30,23/Mar | 64 | 14:30,18/Jul | 20
| XMY MAX | [5 empty] | 52 | 281 | 333 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 08:30,08/Mar | 55 | 06:30,18/Jul | 16
| XMYMIN | [5 empty] | 1211 | 25 | 1236 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 10:30,17/Jan | 57 | 06:30,15/Aug | 18
8 | TMY2 | [5 empty] | 1316 | 97 | 1413 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 06:30,22/Apr | 54 | 09:30,03/Jul | 19
| TMY3 | [5 empty] | 1175 | 163 | 1338 | [5 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 01:30,14/Feb | 49 | 14:30,10/Sep | 22
| TMY3WA | [5 empty] | 671 | 450 | 1121 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 06:30,28/Jan | 59 | 13:30,12/Sep | 21
| TMY7WA | [5 empty] | 955 | 259 | 1214 | [5 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 20:30,11/Dec | 61 | 12:30,18/Jul | 19
| TMY15WA | [5 empty] | 873 | 445 | 1318 | [5 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 08:30,26/Nov | 55 | 19:30,11/Jul | 15
| XMY MAX | [5 empty] | 224 | 955 | 1179 | [5 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 19:30,20/Jan | 54 | 05:30,30/Aug | 17
| XMYMIN | [5 empty] | 1904 | 0 | 1904 | [5 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,15/Apr | 55 | 04:30,02/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 23:30,08/Dec | 51 | 14:30,06/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 06:30,02/Nov | 58 | 14:30,15/Aug | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 08:30,20/Nov | 60 | 18:30,01/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 16:30,31/Jan | 53 | 19:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 14:30,19/Dec | 56 | 04:30,26/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 08:30,20/Apr | 53 | 12:30,11/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 08:30,19/Apr | 46 | 14:30,06/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 06:30,08/Jun | 56 | 14:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 18:30,11/Jan | 59 | 15:30,24/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 12:30,03/Feb | 42 | 05:30,20/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 18:30,20/Jan | 54 | 05:30,20/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 06:30,10/Feb | 55 | 16:30,25/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 20:30,19/Dec | 55 | 14:30,08/Sep | 25
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,01/Feb | 58 | 12:30,04/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 02:30,26/Jan | 59 | 14:30,11/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 08:30,29/Dec | 56 | 05:30,02/Sep | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 08:30,17/Dec | 53 | 23:30,24/Aug | 19
[14 empty] | 3A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 9 | 06:30,04/Jan | 99 | 16:30,12/Jul | 74
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 09:30,20/Feb | 54 | 14:30,06/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 10 | 06:30,04/Jan | 100 | 16:30,06/May | 78
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 14:30,07/Dec | 65 | 11:30,14/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 14:30,04/Dec | 52 | 01:30,26/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 12:30,12/Dec | 62 | 02:30,16/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 21 | 06:30,27/Feb | 99 | 15:30,26/Jul | 78
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 01:30,04/Mar | 51 | 14:30,19/May | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 20 | 05:30,25/Feb | 100 | 14:30,13/May | 82
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 12:30,19/Jan | 65 | 11:30,14/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 14:30,17/Jan | 47 | 20:30,27/Jun | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 13:30,27/Feb | 64 | 23:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 7 | 06:30,15/Feb | 99 | 13:30,09/Sep | 73
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 03:30,07/Mar | 49 | 14:30,09/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 7 | 16:30,14/Feb | 100 | 16:30,06/Jul | 77
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 11:30,28/Dec | 63 | 14:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 10:30,11/Jan | 44 | 20:30,13/Jun | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 17:30,26/Jan | 60 | 03:30,09/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 8 | 07:30,18/Jan | 98 | 17:30,02/Jul | 71
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 08:30,08/Nov | 46 | 14:30,14/May | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 8 | 05:30,19/Jan | 100 | 15:30,02/Jul | 76
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 04:30,28/Oct | 64 | 12:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 14:30,22/Dec | 44 | 21:30,03/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 20:30,29/Jan | 58 | 06:30,04/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 20 | 06:30,07/Feb | 99 | 16:30,12/Jul | 76
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 08:30,03/Mar | 51 | 15:30,07/Sep | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 16 | 05:30,02/Feb | 100 | 16:30,20/May | 80
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 12:30,19/Jan | 65 | 11:30,14/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 14:30,17/Jan | 52 | 01:30,26/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 15:30,24/Jan | 62 | 02:30,16/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 7 | 07:30,22/Feb | 97 | 16:30,09/Aug | 54
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 02:30,03/May | 44 | 16:30,10/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 8 | 17:30,07/Mar | 100 | 16:30,10/Sep | 60
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 14:30,29/Oct | 57 | 16:30,29/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 13:30,03/Feb | 40 | 06:30,24/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 13:30,18/Jan | 49 | 22:30,11/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 46 | 05:30,27/Dec | 100 | 15:30,30/Jun | 88
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 01:30,25/Jan | 55 | 17:30,07/Sep | 29
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 42 | 07:30,07/Feb | 100 | 16:30,29/Apr | 90
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 08:30,03/Jan | 64 | 13:30,08/Aug | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 14:30,25/Dec | 53 | 01:30,26/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 08:30,08/Feb | 61 | 01:30,30/Aug | 22
[14 empty] | 3B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 07:30,22/Mar | 51 | 14:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 01:30,13/Mar | 49 | 13:30,17/Sep | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 06:30,22/Oct | 53 | 11:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 04:30,18/Apr | 56 | 09:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 09:30,13/Nov | 60 | 05:30,20/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 15:30,27/Dec | 55 | 07:30,11/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,28/Oct | 52 | 08:30,22/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 00:30,25/Feb | 49 | 13:30,17/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,18/Mar | 56 | 13:30,07/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 08:30,30/Mar | 57 | 14:30,22/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 09:30,13/Nov | 61 | 05:30,06/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 15:30,07/Jan | 55 | 06:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,02/Apr | 53 | 01:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 09:30,29/Mar | 51 | 14:30,02/Sep | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,15/Apr | 55 | 12:30,07/Aug | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 20:30,03/Feb | 59 | 12:30,07/Aug | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 12:30,06/Nov | 55 | 06:30,13/Dec | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 14:30,15/Feb | 54 | 06:30,07/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 06:30,06/Apr | 51 | 14:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 01:30,26/Mar | 52 | 06:30,11/Jan | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 06:30,02/Apr | 55 | 13:30,07/Aug | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 10:30,08/Feb | 67 | 06:30,11/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 09:30,25/Feb | 69 | 06:30,11/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 17:30,12/Mar | 54 | 06:30,07/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,05/Apr | 53 | 00:30,02/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 08:30,15/Apr | 50 | 14:30,03/Sep | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,18/Mar | 53 | 11:30,11/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 00:30,16/Mar | 56 | 09:30,11/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 09:30,13/Nov | 61 | 05:30,06/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 15:30,23/Dec | 55 | 07:30,11/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 06:30,20/May | 45 | 14:30,31/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 01:30,12/May | 66 | 05:30,18/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 06:30,31/Aug | 52 | 14:30,22/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 08:30,29/May | 79 | 07:30,17/Jan | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 15:30,08/May | 80 | 05:30,18/Jan | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 14:30,02/Dec | 58 | 15:30,17/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 06:30,12/Mar | 51 | 13:30,05/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 01:30,23/Jan | 54 | 14:30,03/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,10/Nov | 56 | 12:30,05/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 00:30,01/Dec | 59 | 14:30,05/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 11:30,20/Nov | 52 | 04:30,24/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 16:30,27/Dec | 53 | 01:30,27/Jul | 17
[14 empty] | 3C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 22 | 05:30,11/Jan | 88 | 14:30,14/Oct | 56
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 02:30,01/Sep | 31 | 06:30,11/Jan | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 23 | 07:30,10/Jan | 98 | 14:30,14/Oct | 62
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 09:30,12/Jan | 26 | 03:30,11/Jan | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 13:30,21/Mar | 27 | 07:30,10/Jan | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 20:30,11/Jan | 25 | 10:30,14/Oct | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 25 | 05:30,09/Feb | 92 | 14:30,05/Oct | 63
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 23:30,30/Jul | 27 | 14:30,05/Oct | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 23 | 05:30,09/Feb | 98 | 14:30,23/Sep | 68
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 14:30,30/Mar | 31 | 15:30,03/Oct | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 09:30,25/Dec | 22 | 05:30,08/Feb | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 19:30,30/Dec | 29 | 06:30,25/Sep | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 24 | 05:30,11/Jan | 89 | 14:30,24/Sep | 57
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 23:30,22/May | 31 | 06:30,11/Jan | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 23 | 07:30,26/Dec | 98 | 15:30,15/Sep | 63
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 04:30,27/Sep | 25 | 05:30,27/Dec | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 09:30,18/Dec | 26 | 05:30,27/Dec | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 12:30,25/Dec | 23 | 10:30,12/May | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 22 | 05:30,26/Dec | 92 | 14:30,30/Sep | 54
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 00:30,13/Sep | 34 | 07:30,26/Dec | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 21 | 07:30,02/Jan | 98 | 16:30,28/Sep | 60
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 08:30,23/Mar | 36 | 14:30,03/Jul | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 13:30,20/Mar | 29 | 05:30,26/Dec | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 09:30,10/Apr | 29 | 04:30,30/Sep | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 28 | 07:30,25/Dec | 92 | 14:30,20/Sep | 58
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 01:30,10/Oct | 27 | 14:30,20/Sep | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 28 | 05:30,20/Jan | 98 | 14:30,17/Sep | 64
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 11:30,10/Mar | 41 | 14:30,19/Sep | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 15:30,17/Jan | 18 | 17:30,31/May | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 08:30,06/Dec | 29 | 19:30,19/Sep | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 20 | 05:30,13/Jan | 79 | 14:30,10/Sep | 44
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 02:30,11/Sep | 37 | 04:30,13/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 20 | 05:30,13/Jan | 94 | 15:30,10/Sep | 51
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 14:30,15/Mar | 28 | 03:30,06/Dec | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 13:30,12/Jun | 30 | 02:30,06/Dec | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 17:30,27/Jan | 19 | 13:30,09/Sep | 7
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 39 | 23:30,03/Jan | 93 | 14:30,30/Sep | 69
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 21:30,04/Dec | 30 | 14:30,13/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 38 | 00:30,04/Jan | 99 | 14:30,13/Sep | 74
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 07:30,18/Mar | 47 | 15:30,29/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 15:30,14/Feb | 22 | 17:30,26/Oct | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 08:30,20/Jan | 36 | 19:30,29/Aug | 12
[14 empty] | 4A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 07:30,27/Oct | 60 | 08:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 00:30,17/Nov | 79 | 14:30,23/Jul | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,19/Oct | 58 | 09:30,25/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 09:30,12/Jan | 63 | 12:30,25/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 14:30,05/Dec | 45 | 07:30,24/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 20:30,04/Mar | 60 | 07:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,04/May | 60 | 08:30,25/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 08:30,02/Apr | 79 | 14:30,23/Jul | 25
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,31/Mar | 58 | 09:30,25/Jul | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 15:30,11/Nov | 63 | 12:30,25/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 10:30,09/Jan | 47 | 17:30,30/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 20:30,28/Jan | 60 | 07:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,22/Apr | 55 | 12:30,05/Sep | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 00:30,02/May | 73 | 16:30,06/Sep | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,20/Oct | 57 | 18:30,05/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 08:30,10/Apr | 64 | 13:30,05/Sep | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 08:30,02/Nov | 44 | 20:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 18:30,04/Feb | 56 | 07:30,11/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,05/May | 55 | 10:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 23:30,18/Oct | 68 | 16:30,09/Aug | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,30/Apr | 59 | 09:30,25/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 20:30,14/Jan | 68 | 10:30,25/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 10:30,09/Jan | 45 | 05:30,18/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 20:30,22/Jan | 58 | 22:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,05/Nov | 60 | 08:30,25/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 06:30,02/Nov | 79 | 14:30,23/Jul | 25
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,17/Mar | 58 | 09:30,25/Jul | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 20:30,12/Feb | 63 | 12:30,25/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 12:30,28/Mar | 45 | 07:30,24/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 15:30,18/Apr | 60 | 07:30,25/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,30/Sep | 39 | 07:30,24/Jan | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 01:30,26/May | 42 | 16:30,08/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,30/Sep | 52 | 18:30,01/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 08:30,12/Jun | 46 | 18:30,01/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 11:30,14/Jan | 45 | 05:30,11/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 13:30,06/Dec | 40 | 19:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,12/Feb | 58 | 04:30,08/Aug | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 08:30,30/Jan | 84 | 18:30,31/May | 34
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,31/Mar | 61 | 14:30,31/Jul | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 07:30,29/Mar | 65 | 13:30,01/Aug | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 15:30,26/Dec | 53 | 00:30,05/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 13:30,14/Feb | 60 | 05:30,08/Aug | 20
[14 empty] | 4B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,17/May | 41 | 16:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 21:30,14/Apr | 77 | 14:30,20/Jul | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,22/Oct | 50 | 14:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 14:30,12/Feb | 54 | 13:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 14:30,27/Jan | 62 | 18:30,02/Sep | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 12:30,14/Mar | 41 | 19:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,25/Mar | 41 | 14:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 01:30,04/Nov | 75 | 14:30,08/Sep | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 06:30,12/May | 54 | 12:30,11/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 10:30,11/Apr | 56 | 13:30,11/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 12:30,14/Mar | 63 | 18:30,02/Sep | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 16:30,19/Jan | 39 | 07:30,01/Aug | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,27/Apr | 44 | 15:30,25/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 21:30,18/Apr | 73 | 14:30,29/Jun | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,11/May | 52 | 15:30,21/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 11:30,19/Mar | 53 | 10:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 16:30,11/Jan | 63 | 18:30,20/May | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 20:30,01/Dec | 43 | 07:30,04/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 06:30,20/Apr | 46 | 21:30,01/Aug | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 09:30,18/Apr | 68 | 15:30,03/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,12/Oct | 53 | 14:30,01/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 12:30,18/Mar | 54 | 15:30,01/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 14:30,10/Apr | 64 | 19:30,20/May | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 18:30,27/Jan | 49 | 22:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,27/Apr | 41 | 16:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 00:30,10/Apr | 77 | 14:30,20/Jul | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 06:30,12/May | 51 | 14:30,28/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 11:30,03/Mar | 54 | 13:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 15:30,07/Nov | 61 | 18:30,24/Sep | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 14:30,23/Jan | 41 | 19:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 06:30,16/Jun | 41 | 04:30,03/Feb | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 00:30,22/May | 67 | 06:30,03/Feb | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,04/Jun | 45 | 16:30,31/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 19:30,22/Feb | 47 | 03:30,03/Feb | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 16:30,23/Mar | 57 | 19:30,31/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 21:30,08/Oct | 40 | 20:30,02/Feb | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,25/Mar | 43 | 18:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 22:30,09/Nov | 80 | 18:30,31/May | 27
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,23/Apr | 52 | 13:30,29/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 11:30,02/Feb | 53 | 14:30,17/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 14:30,06/Mar | 68 | 18:30,31/May | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 19:30,15/Feb | 42 | 19:30,08/Aug | 13
[14 empty] | 4C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,10/Jun | 40 | 15:30,01/Aug | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 21:30,19/Jun | 64 | 16:30,10/Sep | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,14/Oct | 53 | 14:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 15:30,12/Jan | 54 | 14:30,01/Aug | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 09:30,18/Jan | 50 | 17:30,07/May | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 12:30,24/Apr | 38 | 19:30,01/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,04/Oct | 32 | 15:30,15/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 14:30,06/Jun | 59 | 16:30,15/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 06:30,13/Sep | 48 | 14:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 08:30,09/Nov | 43 | 16:30,14/Aug | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 09:30,21/Feb | 51 | 17:30,06/Sep | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 13:30,28/Feb | 29 | 18:30,15/Aug | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 07:30,15/Oct | 34 | 20:30,09/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 01:30,28/Oct | 52 | 16:30,10/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,06/Oct | 49 | 18:30,21/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 02:30,08/Oct | 41 | 16:30,05/Jun | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 13:30,23/May | 48 | 19:30,05/Apr | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 16:30,06/Dec | 35 | 19:30,08/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,09/Apr | 33 | 20:30,09/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 09:30,12/Jun | 52 | 17:30,10/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,04/Oct | 45 | 18:30,09/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 15:30,11/Jan | 42 | 05:30,31/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 09:30,29/Jan | 56 | 19:30,17/May | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 15:30,10/Apr | 35 | 20:30,15/Aug | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,10/Jun | 40 | 15:30,01/Aug | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 21:30,19/Jun | 64 | 16:30,10/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,22/Apr | 53 | 14:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 12:30,08/Jan | 54 | 14:30,01/Aug | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 10:30,02/Dec | 49 | 17:30,07/Sep | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 13:30,13/Mar | 38 | 19:30,01/Aug | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,02/Jul | 35 | 07:30,07/Feb | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 23:30,10/Sep | 40 | 06:30,08/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,15/Sep | 36 | 04:30,08/Dec | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 09:30,27/May | 44 | 02:30,01/Nov | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 12:30,05/Feb | 36 | 07:30,07/Feb | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 15:30,24/Nov | 36 | 07:30,07/Feb | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,16/Apr | 41 | 13:30,15/Aug | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 11:30,17/Apr | 70 | 17:30,02/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,15/Oct | 55 | 14:30,15/Aug | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 09:30,30/Nov | 53 | 16:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 14:30,20/Feb | 59 | 17:30,06/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 14:30,27/Feb | 46 | 19:30,15/Aug | 12
[14 empty] | 5A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY7_WA.aps | Percentage (%) | 5 | 07:30,21/Oct | 49 | 11:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY7_WA.aps | Percentage (%) | 5 | 08:30,11/May | 69 | 16:30,09/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY7_WA.aps | Percentage (%) | 5 | 07:30,27/Oct | 56 | 13:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY7_WA.aps | Percentage (%) | 5 | 07:30,07/Oct | 63 | 11:30,24/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY7_WA.aps | Percentage (%) | 5 | 08:30,09/Apr | 39 | 07:30,24/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY7_WA.aps | Percentage (%) | 5 | 17:30,31/Dec | 52 | 01:30,19/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY3_WA.aps | Percentage (%) | 5 | 07:30,19/Nov | 51 | 18:30,15/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY3_WA.aps | Percentage (%) | 5 | 08:30,16/Nov | 69 | 16:30,13/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY3_WA.aps | Percentage (%) | 5 | 07:30,19/Nov | 55 | 16:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY3_WA.aps | Percentage (%) | 5 | 08:30,25/Nov | 61 | 12:30,29/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY3_WA.aps | Percentage (%) | 5 | 13:30,09/May | 44 | 18:30,23/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY3_WA.aps | Percentage (%) | 5 | 16:30,05/Mar | 51 | 23:30,14/Aug | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY3.aps | Percentage (%) | 5 | 15:30,10/Nov | 53 | 01:30,19/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY3.aps | Percentage (%) | 5 | 01:30,04/May | 69 | 14:30,19/Jul | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY3.aps | Percentage (%) | 5 | 06:30,20/Apr | 57 | 15:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY3.aps | Percentage (%) | 5 | 23:30,05/Oct | 63 | 11:30,17/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY3.aps | Percentage (%) | 5 | 12:30,23/Oct | 47 | 05:30,07/Feb | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY3.aps | Percentage (%) | 5 | 18:30,18/Mar | 59 | 20:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY2.aps | Percentage (%) | 5 | 07:30,01/Oct | 47 | 18:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY2.aps | Percentage (%) | 5 | 01:30,04/May | 60 | 14:30,19/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY2.aps | Percentage (%) | 5 | 07:30,28/Oct | 53 | 19:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY2.aps | Percentage (%) | 5 | 18:30,24/Mar | 59 | 13:30,03/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY2.aps | Percentage (%) | 5 | 11:30,08/Mar | 44 | 18:30,26/May | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY2.aps | Percentage (%) | 5 | 17:30,10/Nov | 50 | 19:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_TMY15_WA.aps | Percentage (%) | 5 | 07:30,19/Nov | 49 | 11:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_TMY15_WA.aps | Percentage (%) | 5 | 08:30,16/Nov | 69 | 16:30,13/Sep | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_TMY15_WA.aps | Percentage (%) | 5 | 07:30,30/Sep | 56 | 13:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_TMY15_WA.aps | Percentage (%) | 5 | 08:30,25/Nov | 63 | 11:30,24/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_TMY15_WA.aps | Percentage (%) | 5 | 14:30,03/Apr | 44 | 18:30,23/Sep | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_TMY15_WA.aps | Percentage (%) | 5 | 12:30,06/Nov | 52 | 01:30,19/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_MIN_WA.aps | Percentage (%) | 5 | 07:30,16/Sep | 42 | 04:30,31/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_MIN_WA.aps | Percentage (%) | 5 | 20:30,18/Sep | 43 | 07:30,31/Jan | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_MIN_WA.aps | Percentage (%) | 5 | 07:30,16/Sep | 41 | 05:30,31/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_MIN_WA.aps | Percentage (%) | 5 | 21:30,02/Jun | 46 | 03:30,31/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_MIN_WA.aps | Percentage (%) | 5 | 21:30,01/Nov | 47 | 00:30,31/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_MIN_WA.aps | Percentage (%) | 5 | 18:30,02/Apr | 40 | 01:30,18/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | 5A_MAX_WA.aps | Percentage (%) | 5 | 07:30,12/Nov | 58 | 02:30,19/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | 5A_MAX_WA.aps | Percentage (%) | 5 | 09:30,11/Mar | 79 | 17:30,02/Sep | 26
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | 5A_MAX_WA.aps | Percentage (%) | 5 | 07:30,28/Apr | 58 | 14:30,07/Aug | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | 5A_MAX_WA.aps | Percentage (%) | 5 | 12:30,04/Feb | 62 | 13:30,22/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | 5A_MAX_WA.aps | Percentage (%) | 5 | 08:30,11/Feb | 48 | 01:30,26/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | 5A_MAX_WA.aps | Percentage (%) | 5 | 17:30,15/Jan | 59 | 03:30,19/Jul | 17
[14 empty] | 5B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,21/Jun | 41 | 01:30,07/Feb | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,19/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 06:30,11/Aug | 50 | 14:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 16:30,25/Jan | 51 | 15:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 12:30,04/Mar | 52 | 17:30,03/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 11:30,10/Apr | 39 | 07:30,07/Feb | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 06:30,07/Jun | 38 | 04:30,24/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,19/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 06:30,11/Aug | 50 | 14:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 18:30,08/Jan | 51 | 15:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 12:30,13/Jan | 52 | 17:30,03/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 12:30,21/Mar | 35 | 05:30,23/Dec | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 22:30,10/Jun | 42 | 04:30,13/Dec | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 23:30,05/Oct | 69 | 16:30,09/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,14/Sep | 47 | 13:30,01/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 00:30,11/May | 49 | 16:30,27/Jun | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 10:30,13/Nov | 63 | 19:30,28/May | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 17:30,27/Jan | 39 | 21:30,17/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,08/Jun | 42 | 04:30,13/Dec | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 01:30,10/Jun | 70 | 17:30,02/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,04/Oct | 48 | 14:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 22:30,29/May | 50 | 16:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 11:30,01/Mar | 65 | 18:30,02/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 15:30,13/Nov | 42 | 19:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,03/Jun | 38 | 04:30,24/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 19:30,27/Oct | 52 | 14:30,03/Sep | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 06:30,23/Aug | 46 | 14:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 18:30,08/Jan | 49 | 14:30,25/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 11:30,31/Dec | 54 | 18:30,28/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 12:30,21/Mar | 38 | 04:30,24/Dec | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,12/Jul | 45 | 04:30,06/Dec | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 22:30,12/Aug | 51 | 05:30,02/Feb | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,20/Jul | 44 | 04:30,02/Feb | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 16:30,05/Mar | 48 | 03:30,06/Dec | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 11:30,17/Nov | 48 | 04:30,06/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 20:30,14/Jun | 41 | 05:30,06/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 06:30,05/May | 38 | 15:30,25/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 09:30,20/Apr | 64 | 15:30,03/Sep | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,23/Sep | 48 | 14:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 13:30,07/Dec | 50 | 12:30,25/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 11:30,03/Apr | 63 | 18:30,31/May | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 17:30,02/Feb | 35 | 18:30,25/Jul | 11
[14 empty] | 5C | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 07:30,07/Oct | 30 | 04:30,04/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 23:30,24/Jun | 36 | 16:30,15/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,04/Oct | 36 | 15:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 10:30,12/Apr | 40 | 00:30,01/Feb | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 07:30,24/May | 36 | 17:30,15/Sep | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 17:30,06/Dec | 25 | 10:30,07/Sep | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,17/May | 28 | 04:30,27/Dec | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 22:30,08/May | 48 | 18:30,28/May | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,28/Oct | 46 | 15:30,25/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 12:30,15/Jan | 32 | 16:30,25/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 14:30,20/Mar | 61 | 18:30,28/May | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 17:30,07/Dec | 30 | 10:30,09/Sep | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 06:30,16/Jun | 45 | 12:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 10:30,09/Oct | 62 | 17:30,20/Jul | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,30/Apr | 53 | 15:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 14:30,11/Oct | 63 | 14:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 12:30,26/Sep | 49 | 01:30,08/Mar | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 17:30,16/Nov | 51 | 04:30,21/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,29/Apr | 30 | 15:30,11/Jul | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 23:30,18/Jun | 36 | 15:30,11/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,29/Sep | 52 | 14:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 11:30,01/Apr | 50 | 14:30,11/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 07:30,24/May | 31 | 23:30,31/Oct | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 16:30,04/Nov | 32 | 19:30,11/Jul | 8
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,27/Aug | 39 | 03:30,20/Dec | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 23:30,03/Sep | 46 | 05:30,20/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,27/Aug | 38 | 03:30,04/Jan | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 12:30,15/Apr | 43 | 16:30,07/Feb | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 15:30,15/Jan | 46 | 05:30,20/Dec | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 19:30,01/Apr | 38 | 02:30,20/Dec | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,29/Apr | 31 | 15:30,11/Jul | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 15:30,17/Oct | 56 | 19:30,28/May | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,08/Apr | 53 | 14:30,11/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 21:30,12/Mar | 52 | 18:30,11/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 13:30,24/Oct | 64 | 19:30,28/May | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 13:30,24/Oct | 38 | 19:30,11/Jul | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | doeCWEC.aps | Percentage (%) | 5 | 07:30,14/May | 34 | 04:30,22/Nov | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | doeCWEC.aps | Percentage (%) | 5 | 01:30,16/Oct | 33 | 04:30,22/Nov | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | doeCWEC.aps | Percentage (%) | 5 | 07:30,22/Oct | 42 | 16:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | doeCWEC.aps | Percentage (%) | 5 | 07:30,08/Jul | 43 | 03:30,22/Nov | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | doeCWEC.aps | Percentage (%) | 5 | 15:30,02/May | 34 | 03:30,22/Nov | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | doeCWEC.aps | Percentage (%) | 5 | 19:30,29/Oct | 26 | 04:30,22/Nov | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | CWEC.aps | Percentage (%) | 5 | 07:30,14/May | 33 | 03:30,22/Nov | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | CWEC.aps | Percentage (%) | 5 | 01:30,16/Oct | 33 | 04:30,22/Nov | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | CWEC.aps | Percentage (%) | 5 | 07:30,22/Oct | 41 | 15:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | CWEC.aps | Percentage (%) | 5 | 21:30,10/Mar | 43 | 03:30,22/Nov | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | CWEC.aps | Percentage (%) | 5 | 15:30,02/May | 34 | 03:30,22/Nov | 9
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | CWEC.aps | Percentage (%) | 5 | 16:30,24/Dec | 26 | 04:30,22/Nov | 9
[14 empty] | 6A | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,13/May | 45 | 13:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 22:30,04/Oct | 67 | 17:30,09/Sep | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,13/Oct | 58 | 13:30,08/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 01:30,03/Sep | 63 | 17:30,04/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 09:30,22/Mar | 48 | 05:30,24/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 19:30,03/Nov | 48 | 19:30,04/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,21/Apr | 52 | 11:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 15:30,07/Nov | 68 | 18:30,18/Jul | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,16/Apr | 59 | 11:30,18/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 19:30,23/Feb | 65 | 12:30,17/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 13:30,13/Mar | 49 | 17:30,21/May | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 15:30,24/Oct | 59 | 19:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 06:30,07/May | 50 | 12:30,04/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 01:30,05/May | 65 | 17:30,19/Jul | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,19/Apr | 56 | 15:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 20:30,01/Dec | 64 | 14:30,01/Aug | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 12:30,20/Dec | 50 | 04:30,31/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 17:30,01/Mar | 57 | 20:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,10/May | 47 | 12:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 15:30,03/Oct | 64 | 18:30,28/May | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,26/Mar | 52 | 17:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 16:30,16/Mar | 61 | 16:30,17/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 15:30,25/Sep | 48 | 07:30,10/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 17:30,19/Nov | 49 | 07:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 06:30,13/May | 50 | 17:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 04:30,06/Oct | 66 | 18:30,04/Jul | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,13/Oct | 58 | 15:30,03/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 21:30,08/Apr | 61 | 11:30,08/Aug | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 08:30,24/Mar | 42 | 19:30,04/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 13:30,02/Oct | 57 | 19:30,04/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,25/Jun | 44 | 04:30,01/Feb | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 08:30,28/Jun | 45 | 06:30,21/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,25/Jun | 44 | 04:30,21/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 12:30,17/May | 51 | 05:30,01/Feb | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 11:30,15/Mar | 49 | 06:30,03/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 15:30,26/Sep | 40 | 04:30,31/Jan | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,08/Apr | 58 | 19:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 09:30,26/Nov | 85 | 19:30,18/Jul | 29
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,15/Oct | 60 | 17:30,18/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 14:30,08/Jan | 65 | 13:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 10:30,03/Mar | 63 | 05:30,19/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 13:30,20/Nov | 60 | 18:30,18/Jul | 17
[14 empty] | 6B | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 10 | 07:30,23/Jul | 63 | 04:30,10/May | 36
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 32 | 07:30,19/Jan | 93 | 19:30,07/Apr | 65
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 8 | 07:30,19/Jan | 60 | 03:30,05/Apr | 37
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 11 | 21:30,24/Dec | 78 | 18:30,24/May | 37
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 9 | 08:30,19/Jan | 54 | 05:30,06/Apr | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 15 | 07:30,28/Jul | 84 | 13:30,03/Sep | 38
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 07:30,02/Jun | 38 | 17:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 23:30,07/Oct | 63 | 16:30,22/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,27/May | 53 | 15:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 03:30,11/Jul | 52 | 16:30,18/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 13:30,15/Mar | 59 | 18:30,01/Sep | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 16:30,22/Mar | 39 | 19:30,18/Jul | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 07:30,20/May | 40 | 01:30,27/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 09:30,15/May | 55 | 17:30,15/Sep | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,22/Jun | 50 | 15:30,08/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 20:30,03/Dec | 47 | 16:30,08/Aug | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 14:30,22/Jan | 58 | 18:30,25/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 16:30,08/Mar | 39 | 01:30,18/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,11/Jun | 43 | 05:30,12/Dec | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 01:30,18/Jun | 57 | 15:30,30/Jun | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,01/Sep | 48 | 15:30,26/Jun | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 11:30,20/Apr | 50 | 06:30,12/Dec | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 08:30,05/Oct | 54 | 17:30,02/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 18:30,30/Dec | 40 | 05:30,13/Dec | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,17/Jun | 35 | 04:30,30/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 08:30,23/Jun | 57 | 14:30,29/Jul | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,24/Sep | 46 | 14:30,25/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 18:30,12/Jan | 50 | 14:30,24/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 09:30,24/May | 58 | 18:30,02/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 12:30,16/Oct | 37 | 05:30,30/Dec | 10
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,11/Aug | 43 | 04:30,06/Dec | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 22:30,11/Aug | 48 | 06:30,17/Feb | 23
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,11/Aug | 45 | 04:30,17/Feb | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 17:30,04/Mar | 50 | 04:30,20/Dec | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 17:30,08/Jun | 49 | 02:30,05/Dec | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 10:30,04/Sep | 42 | 05:30,18/Feb | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 06:30,12/May | 40 | 13:30,01/Aug | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 22:30,28/Oct | 68 | 14:30,16/Jul | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,21/Sep | 50 | 12:30,01/Aug | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 19:30,09/Feb | 49 | 13:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 13:30,13/Mar | 65 | 18:30,03/Sep | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 11:30,06/Nov | 41 | 19:30,01/Aug | 11
[14 empty] | 7 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 07:30,22/Sep | 42 | 13:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 23:30,06/Oct | 55 | 14:30,07/Sep | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,21/Sep | 51 | 15:30,04/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 10:30,20/Oct | 59 | 16:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 11:30,19/Jan | 46 | 07:30,03/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 18:30,02/Nov | 46 | 07:30,04/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 06:30,25/May | 47 | 16:30,04/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 22:30,13/May | 58 | 15:30,31/May | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,24/Mar | 57 | 16:30,04/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 13:30,07/Apr | 60 | 11:30,04/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 11:30,25/Jan | 49 | 17:30,05/May | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 17:30,22/Nov | 48 | 07:30,04/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 07:30,12/May | 42 | 03:30,20/Dec | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 23:30,29/Sep | 44 | 16:30,26/May | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,10/Sep | 54 | 14:30,17/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 20:30,22/Mar | 57 | 16:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 12:30,26/Feb | 49 | 00:30,20/Dec | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 18:30,13/Apr | 45 | 18:30,18/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,24/Jun | 43 | 04:30,01/Feb | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 21:30,05/Jun | 47 | 16:30,08/Jul | 19
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,23/Jun | 50 | 16:30,11/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 09:30,12/May | 51 | 05:30,08/Feb | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 14:30,12/Feb | 49 | 01:30,01/Feb | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 19:30,02/Nov | 43 | 20:30,11/Jul | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,15/Oct | 51 | 10:30,18/Jul | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 23:30,15/Apr | 60 | 12:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,30/Sep | 57 | 12:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 20:30,19/Feb | 65 | 12:30,17/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 11:30,01/Mar | 37 | 05:30,25/Jan | 11
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 12:30,13/Nov | 53 | 07:30,18/Jul | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,20/Aug | 45 | 18:30,17/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 09:30,12/Aug | 47 | 19:30,17/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,27/Jul | 46 | 07:30,17/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 19:30,26/Mar | 51 | 22:30,17/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 16:30,23/Mar | 49 | 07:30,17/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 16:30,07/Oct | 43 | 22:30,17/Jan | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,26/Apr | 56 | 09:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 23:30,11/Apr | 73 | 13:30,18/Jul | 24
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,15/Oct | 59 | 13:30,18/Jul | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 13:30,05/Apr | 64 | 10:30,18/Jul | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 10:30,13/Mar | 50 | 17:30,29/Sep | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 15:30,03/Apr | 56 | 19:30,18/Jul | 15
[14 empty] | 8 | Var. Name | Location | Filename | Type | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY7WA.aps | Percentage (%) | 5 | 06:30,20/Aug | 44 | 03:30,28/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY7WA.aps | Percentage (%) | 5 | 00:30,04/Sep | 45 | 04:30,28/Jan | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY7WA.aps | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,26/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY7WA.aps | Percentage (%) | 5 | 23:30,19/May | 48 | 05:30,19/Dec | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY7WA.aps | Percentage (%) | 5 | 10:30,13/Jun | 55 | 19:30,26/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY7WA.aps | Percentage (%) | 5 | 17:30,02/Apr | 43 | 20:30,27/Jan | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3WA.aps | Percentage (%) | 5 | 06:30,02/Sep | 42 | 00:30,06/Dec | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3WA.aps | Percentage (%) | 5 | 00:30,11/Sep | 54 | 16:30,28/Jun | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3WA.aps | Percentage (%) | 5 | 07:30,27/Aug | 51 | 15:30,19/Jun | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3WA.aps | Percentage (%) | 5 | 10:30,28/Apr | 50 | 15:30,19/Jun | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3WA.aps | Percentage (%) | 5 | 14:30,05/Mar | 52 | 18:30,12/May | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3WA.aps | Percentage (%) | 5 | 17:30,08/Apr | 41 | 21:30,27/Jun | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY3.aps | Percentage (%) | 5 | 07:30,19/May | 44 | 04:30,01/Mar | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY3.aps | Percentage (%) | 5 | 22:30,19/Aug | 45 | 04:30,01/Mar | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY3.aps | Percentage (%) | 5 | 07:30,20/Aug | 46 | 04:30,12/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY3.aps | Percentage (%) | 5 | 16:30,11/Mar | 52 | 04:30,01/Mar | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY3.aps | Percentage (%) | 5 | 10:30,21/Aug | 50 | 20:30,05/Dec | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY3.aps | Percentage (%) | 5 | 17:30,29/Sep | 41 | 02:30,01/Mar | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY2.aps | Percentage (%) | 5 | 07:30,03/Jun | 49 | 04:30,04/Jan | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY2.aps | Percentage (%) | 5 | 09:30,13/Jun | 50 | 05:30,04/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY2.aps | Percentage (%) | 5 | 07:30,27/Aug | 49 | 01:30,04/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY2.aps | Percentage (%) | 5 | 13:30,18/May | 55 | 01:30,04/Jan | 18
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY2.aps | Percentage (%) | 5 | 15:30,19/Mar | 52 | 04:30,03/Jan | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY2.aps | Percentage (%) | 5 | 20:30,22/Apr | 47 | 05:30,04/Jan | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | TMY15WA.aps | Percentage (%) | 5 | 07:30,21/May | 40 | 06:30,21/Feb | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | TMY15WA.aps | Percentage (%) | 5 | 09:30,23/Sep | 54 | 16:30,28/Jun | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | TMY15WA.aps | Percentage (%) | 5 | 07:30,22/Sep | 51 | 15:30,19/Jun | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | TMY15WA.aps | Percentage (%) | 5 | 18:30,12/Feb | 50 | 15:30,19/Jun | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | TMY15WA.aps | Percentage (%) | 5 | 10:30,28/Oct | 47 | 04:30,21/Feb | 12
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | TMY15WA.aps | Percentage (%) | 5 | 17:30,07/Apr | 41 | 21:30,27/Jun | 13
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MIN.aps | Percentage (%) | 5 | 07:30,02/Jul | 49 | 03:30,18/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MIN.aps | Percentage (%) | 5 | 11:30,15/Jul | 51 | 06:30,11/Jan | 26
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MIN.aps | Percentage (%) | 5 | 07:30,16/Jul | 50 | 04:30,11/Jan | 21
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MIN.aps | Percentage (%) | 5 | 13:30,03/Sep | 56 | 05:30,11/Jan | 22
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MIN.aps | Percentage (%) | 5 | 12:30,12/Oct | 52 | 04:30,01/Feb | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MIN.aps | Percentage (%) | 5 | 17:30,31/Aug | 47 | 05:30,11/Jan | 16
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 1 | MAX.aps | Percentage (%) | 5 | 07:30,24/Sep | 40 | 20:30,27/Jun | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - MECH | MAX.aps | Percentage (%) | 5 | 01:30,02/Oct | 68 | 18:30,28/May | 20
[15 empty] | People dissatisfied | ASHRAE ZONING - FLOOR 2 | MAX.aps | Percentage (%) | 5 | 07:30,31/Aug | 51 | 15:30,20/Jun | 17
[15 empty] | People dissatisfied | ASHRAE ZONING - AUDITORIUM | MAX.aps | Percentage (%) | 5 | 10:30,08/Oct | 50 | 16:30,03/Jul | 15
[15 empty] | People dissatisfied | ASHRAE ZONING - GYM | MAX.aps | Percentage (%) | 5 | 10:30,12/Sep | 66 | 18:30,25/May | 14
[15 empty] | People dissatisfied | ASHRAE ZONING - KITCHEN CAFETERIA | MAX.aps | Percentage (%) | 5 | 14:30,09/Oct | 45 | 22:30,27/Jun | 12